## Summary Sheet(OLD) (hidden)
Description | Amount
2. Site Preparation & Fencing | 0
3. Roads & Stormwater | 0
4. Reservoir | 0
5. Chambers & Boxes | 0
6. Interconnecting Pipework | 12936500
7. Guard House | 0
8. Telemetry Hut | 0
9. Valve Building | 0
10. Elec & C&I | #REF!
Sub Total A | #REF!
P & G (20%) | #REF!
Sub Total A | #REF!
Escalation (10%) | #REF!
Sub Total A | #REF!
Contingencies (10%) | #REF!
Total | #REF!

## Fee Calc (hidden)
CONTRACT NO. : |  | EI1306
CONTRACT NAME : |  | CARLSWALD 10ML RESERVOIR
CLIENT : |  | JOHANNESBURG WATER (SOC) Ltd.
ZC PROJECT NUMBER : |  |  |  |  | 13214
PROJECT BUDGET : SUMMARY
Fee Calculation:
FEE: | Cost of Works x %Fee x Fee Adj. Factor
Estimated Cost of Works : |  | #REF! | (Excluding VAT)
%Fee = | 10%
Fee Adj. Factor = [1 - 0.2] = |  | 0.8
Fees = | #REF! | (Excluding VAT)
NO. | DESCRIPTION |  |  |  | VALUE
Professional Fees
1 | Inception |  |  | 5% | #REF!
2 | Concept and Viability |  |  | 25% | #REF!
3 | Design Development |  |  | 30% | #REF!
4 | Documentation and Procurement |  |  | 10% | #REF!
5 | Contract Administration and Inspection |  |  | 25% | #REF!
6 | Close Out |  |  | 5% | #REF!
| SUBTOTAL (FEES) |  |  |  | #REF!
7 | Construction Monitoring (months) |  | 15 | 50000 | 750000
Disbursements
8 | Geotechnical Investigation |  |  | 29800 | 29800
9 | Topographical Survey |  |  | 9570.75 | 9570.75
10 | Sub-Division |  |  | 63550 | 63550
11 | Rezoning |  |  | 40476 | 40476
12 | Handling Fee |  |  | 10% | 14339.675
| SUBTOTAL (DISBURSEMENTS) |  |  |  | 157737
| SUBTOTAL : PROFESSIONAL FEES |  |  |  | #REF!
Construction Works
11 | Estimated Cost of Works |  |  |  | #REF!
| TOTAL (EXCL. VAT) |  |  |  | #REF!
| VAT |  |  | 15% | #REF!
| TOTAL (INCL. VAT) |  |  |  | #REF!

## PS - SCOUR PIPE DETAIL (hidden)
PROJECT NUMBER: EI1306
CARLSWALD 20ML RESERVOIR
SECTION 6: |  | INTERCONNECTING PIPEWORK
(SCOUR PIPE DETAIL- DWG 13214-73-04-003)
Mark on dwg | NB (mm) | Mat | Decription | Sketch | No. | Rate | Amount
SP-001 | 150 | S.S | 90° SHORT RADIUS BEND ONE END 230mm C. TO F. OTHER END WITH BELLMOUTH O.A 1850mm LONG |  | 1
SP-002 | 150 | S.S | FLANGED PIPE O.A 3300mm |  | 1
SUB TOTAL CARRIED FORWARD | [6 empty] | 0

## PS - OVERFLOW PIPING (hidden)
PROJECT NUMBER: EI1306
CARLSWALD 20ML RESERVOIR
SECTION 6: |  | INTERCONNECTING PIPEWORK
(OVERFLOW PIPING DETAILS - DWG 13214-73-04-003)
Mark on dwg | NB (mm) | Mat | Decription | Sketch | No. | Rate | Amount
OF-001 | 350 | S.S | FLANGED BELLMOUTH O.A 600mm BELLMOUTH 550mm DIA. |  | 1
OF-002 | 350 | S.S | FLANGED 90° SHORT RADIUS BEND. ONE END 360mm C. to F. OTHER 3620mm C. to F. |  | 1
OF-003 | 350 | S.S | FLANGED PIPE O.A 3100mm |  | 1
SUB TOTAL CARRIED FORWARD | [6 empty] | 0

## PS- DRAIN PIPING (hidden)
PROJECT NUMBER: EI1306
CARLSWALD 20ML RESERVOIR
SECTION 6: |  | INTERCONNECTING PIPEWORK
(DRAIN PIPING- DWG 13214-73-04-003)
Mark on dwg | NB (mm) | Mat | Decription | Sketch | No. | Rate | Amount
DR-001 | 150 | S.S | FLANGED 90° SHORT RADIUS BEND. ONE END 230mm C. TO F. OTHER END PLAIN 3620mm O.A WITH PUDDLE FLANGE 125mm FROM PLAIN END |  | 1
DR-002 | 150 | S.S | FLANGED PIPE O.A 2950mm |  | 1
DR-003 | 150 | S.S | FLANGED 45° MEDIUM RADIUS BEND 230mm C. TO F. |  | 1
DR-004 | 150 | S.S | FLANGED PIPE 0.A 6000mm |  | 2 | 60000 | 120000
DR-005 | 150 | S.S | FLANGED PIPE O.A 5430mm |  | 1
SUB-TOTAL CARRIED FORWARD | [6 empty] | 120000
Note on C14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: LC BOQ - EPOXY MILD STEEL

## PS- VALVE BUILDING (hidden)
PROJECT NUMBER: EI1306
CARLSWALD 20ML RESERVOIR
SECTION 6: |  | INTERCONNECTING PIPEWORK
(VALVE BUILDING- DWG 13214-73-05-004/005/006)
Mark on dwg | NB (mm) | Mat | Decription | Sketch | No. | Rate | Amount
VB-001 | 600 | S.S | PUDDLE PIPE O.A 900mm BOTH ENDS FLANGED WITH PUDDLE FLANGE 450mm FROM ONE END. |  | 2 | 85000 | 170000
VB-002 | 600 | S.S | STANDARD FLANGED 90° Y-PIECE, BRANCH 1265mm C TO F. 50mm TAP OFF 320mm FROM FLANGED END |  | 1
VB-003 | 600 | S.S | STANDARD D.F 45° SHORT RADIUS BEND, 610mm C TO F. |  | 4 | 75000 | 300000
VB-004 | 600 | S.S | FLANGED PIPE O.A 730mm |  | 2
VB-005 | 600 | S.S | FLANGE ADAPTOR |  | 2 | 25000 | 50000
VB-006 | 600 | S.S | UN-EQUAL TEE TWO BRANCHES 610mm C. TO F. PLAIN BRANCH 2950mm O.A 3560mm. |  | 2 | 110000 | 220000
VB-007 | 100X 600 | S.S | FLANGED 100⌀ PIPE O.A 335mm. ONE END WITH 600⌀ FLANGE |  | 2
VB-008 | 600 | S.S | STANDARD FLANGED 90°Y-PIECE BRANCHS 1265 mm C TO F |  | 1 | 125000 | 125000
VB-009 | 150 | S.S | FLANGED PIPE O.A. 1940mm |  | 1
VB-010 | 500 | S.S | PUDDLE PIP O.A 900mm. BOTH ENDS FLANGED WITH PUDDLE FLANGE 450mm FROM ONE END. |  | 2 | 50000 | 100000
VB-011 | 500 | S.S | STANDARD FLANGED 90° Y-PIECE, BRANCH'S 1100mm C. TO F. 50mm TAP OFF 300mm FROM FLANGED END. |  | 1 | 85000 | 85000
SUB-TOTAL CARRIED FORWARD | [6 empty] | 1050000
SUB-TOTAL BROUGHT FORWARD | [6 empty] | 1050000
VB-012 | 500 | S.S | STANDARD D.F 45° SHORT RADIUS BEND 510mm C. TO F. |  | 4 | 48000 | 192000
VB-013 | 500X300 | S.S | FLANGED ECCENTRIC REDUCER O.A 1110mm |  | 2
VB-014 | 300 |  | FLANGE ADAPTOR |  | 4 | 10000 | 40000
VB-015 | 300 | S.S | PIPE ONE END FLANGED O.A 800mm |  | 2
VB-016 | 300 | S.S | FLANGED PIPE 0.A. 2000mm. |  | 2
VB-017 | 500 | S.S | STANDARD FLANGED 90° Y-PIECE, BRANCH'S 1100mm C. TO F. 50mm TAP OFF 300mm FROM FLANGED END TOP AND BOTTOM OF Y-PIECE |  | 1
V-005 | 600 |  | ACTUATED FLANGED WEDGE GATE VALVE |  | 2 | 350000 | 700000
V-006 | 100 |  | FLANGED BALL VALVE |  | 2 | 6000 | 12000
V-007 | 100 |  | AIR RELEASE VALVE | X | 2 | 100000 | 200000
V-008 | 600 |  | NON-RETURN VALVE |  | 2 | 455000 | 910000
V-009 | 300 |  | GEARED FLANGED WEDGE GATE VALVE |  | 2 | 100000 | 200000
V-010 | 300 |  | HYTROL VALVE | X | 2
V-011 | 300 |  | INLINE STRAINER | X | 2 | 50000 | 100000
SUB-TOTAL CARRIED FORWARD | [6 empty] | 3404000
SUB-TOTAL BROUGHT FORWARD | [6 empty] | 3404000
V-012 | 50 |  | THREADED BALL VALVE |  | 2 | 3000 | 6000
V-013 | 50 |  | AIR RELEASE VALVE | X | 2
SUB-TOTAL CARRIED FORWARD | [6 empty] | 8930000

## PS- SCOURBOX (hidden)
PROJECT NUMBER: EI1306
CARLSWALD 20ML RESERVOIR
SECTION 6: |  | INTERCONNECTING PIPEWORK
(SCOURBOX - DWG 13214-73-04-011)
Mark on dwg | NB (mm) | Mat | Decription | Sketch | No. | Rate | Amount
SB-001 | 150 | S.S | PUDDLE PIPE O.A 1100mm. BOTH ENDS FLANGED WITH PUDDLE FLANGE 440mm FROM ONE END. |  | 1 | 10500 | 10500
SB-002 | 150 | S.S | PUDDLE PIPE O.A 1100mm. BOTH ENDS FLANGED WITH PUDDLE FLANGE 440mm FROM ONE END. WITH 50mm TAP OFF. |  | 1 | 15000 | 15000
SB-003 | 350 | S.S | PUDDLE PIPE 0.A 2400mm. ONE END FLANGED WITH PUDDLE FLANGE 465mm FROM FLAGED END. |  | 1 | 30000 | 30000
SB-004 | 150 | S.S | PUBBLE PIPE 0.A 955mm. BOTH ENDS PLAIN WITH PUDDLE FLANGED 705mm FROM END. |  | 2 |  | 0
SB-005 | 150 |  | FLANGED ADAPTOR |  | 2
V-001 | 150 |  | FLANGED WEDGE GATE VALVE |  | 2 | 50000 | 100000
V-002 | 50 |  | BALL VALVE |  | 1 | 3000 | 3000
SUB-TOTAL CARRIED FORWARD | [6 empty] | 55500
Note on F17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2

## PS - FLOW CHAMBERS (hidden)
PROJECT NUMBER: EI1306
CARLSWALD 20ML RESERVOIR
SECTION 6: |  | INTERCONNECTING PIPEWORK
(FLOW METER CHAMBERS- DWG 13214-73-04-005)
Mark on dwg | NB (mm) | Mat | Decription | Sketch | No. | Rate | Amount
IFC-001 | 500 | S.S | PUDDLE PIPE O.A. 900mm. BOTH ENDS FLANGED WITH PUDDLE FLANGE 450mm FROM ONE END. |  | 2 | 55000 | 110000
IFC-002 | 500 | S.S | FLANGED PIPE O.A. 2100mm |  | 1
IFC-003 | 500 |  | FLANGE ADAPTOR |  | 1 | 20000 | 20000
V-003 | 500 |  | CLAMP ON FLOW METER | X | 1
OFC-001 | 500 | S.S | PUDDLE PIPE O.A 900mm. BOTH ENDS FLANGED WITH PUDDLE FLANGE 450mm FROM ONE END. |  | 2
OFC-002 | 500 | S.S | PIPE ONE END FLANGED O.A 2100mm |  | 1
OFC-003 | 500 |  | FLANGE ADAPTOR |  | 1
V-004 | 500 |  | CLAMP ON FLOW METER | X | 1
IP-001 | 500 | COATED M.S. | FLANGED PIPE O.A 600mm |  | 13 | 60000 | 780000
IP-002 | 500 | COATED M.S. | PIPE PME EMD FLANGED O.A 4400mm |  | 1
IP-003 | 500 | COATED M.S. | FLANGED PIPE O.A 5000mm |  | 1
IP-004 | 500 | COATED M.S. | FLANGED PIPE O.A 3200mm |  | 1 | 50000 | 50000
SUB-TOTAL CARRIED FORWARD | [6 empty] | 960000
SUB-TOTAL BROUGHT FORWARD | [6 empty] | 960000
IP-005 | 500 | COATED M.S. | FLANGED PIPE O.A 1100mm |  | 1 | 35000 | 35000
IP-006 | 500 | COATED M.S. | FLANGED PIPE O.A 185mm |  | 1
IP-006 | 500 | COATED M.S. | FLANGED PIPE O.A 3670mm |  | 1
IP-007 | 500 | COATED M.S. | FLANGED 90° MEDIUM RADIUS BEND. ONE END 1020mm c. TO F. OTHER END 6000mm C. TO F. |  | 1
IP-008 | 500 | COATED M.S. | FLANGED 90° SHORT RADIUS BEND. ONE END 5035mm C. TO F. OTHER END 510mm C. TO F. |  | 1 | 55000 | 55000
IP-009 | 500 | COATED M.S. | PUDDLE PIPE, PUDDLE FLANGE 690mm FROM FLANGED END WITH PLAIN EDED 90° SHORT RADIUS BEND 510mm C. TO F. |  | 1
IP-010 | 500 | COATED M.S. | FLANGED 90° MEDIUM RADIUS BEND. 1020MM C. TO F. |  | 1 | 60000 | 60000
IP-011 | 500 |  | FLANGE ADAPTOR |  | 1 | 20000 | 20000
OP-001 | 600 | COATED M.S | FLANGED PIPE O.A 6000mm |  | 15 | 70000 | 1050000
OP-002 | 600 | COATED M.S | PIPE ONE END FLANGED O.A 4400mm |  | 1 | 60000 | 60000
SUB-TOTAL CARRIED FORWARD | [6 empty] | 2240000
SUB-TOTAL BROUGHT FORWARD | [6 empty] | 2240000
OP-003 | 600 | COATED M.S | FLANGED PIPE O.A 3190mm |  | 1 | 50000 | 50000
OP-004 | 600 | COATED M.S | FLANGED PIPE O.A 4440mm |  | 1 | 60000 | 60000
OP-005 | 600 | COATED M.S | FLANGED PIPE O.A 3580mm |  | 1
OP-006 | 600 | COATED M.S | FLANGED 90° MEDIUM RADIUS BEND. ONE END 1020mm C. TO F. OTHER END WITH BELLMOUTH O.A 3695mm |  | 1 |  | 0
OP-007 | 600 | COATED M.S | FLANGED 90° MEDIUM RADIUS BEND. 1020mm C. TO F. |  | 1 | 45000 | 45000
OP-008 | 600 |  | FLANGE ADAPTOR |  | 1 | 25000 | 25000
SUB-TOTAL CARRIED FORWARD | [6 empty] | 2420000

## Pipe Schedule00 (hidden)
PROJECT NUMBER: EI1306
CARLSWALD 20ML RESERVOIR
SECTION 6: |  | INTERCONNECTING PIPEWORK
(OVERFLOW PIPING DETAILS - DWG 13214-73-04-003)
Mark on dwg | NB (mm) | Mat | Decription | Sketch | No. | Rate | Amount
OF-001 | 350 | S.S | FLANGED BELLMOUTH O.A 600mm BELLMOUTH 550mm DIA. |  | 1
OF-002 | 350 | S.S | FLANGED 90° SHORT RADIUS BEND. ONE END 360mm C. to F. OTHER 3620mm C. to F. |  | 1
OF-003 | 350 | S.S | FLANGED PIPE O.A 3100mm |  | 1
SUB-TOTAL CARRIED FORWARD | [6 empty] | 0
|  | brought forward |  |  |  |  | 0
SCOUR PIPING
SP-001 | 150 | S.S | 90° SHORT RADIUS BEND ONE END 230mm C. TO F. OTHER END WITH BELLMOUTH O.A 1850mm LONG |  | 1
SP-002 | 150 | S.S | FLANGED PIPE O.A 3300mm |  | 1
SCOUR BOX
SB-001 | 150 | S.S | PUDDLE PIPE O.A 1100mm. BOTH ENDS FLANGED WITH PUDDLE FLANGE 440mm FROM ONE END. |  | 1 | 10500 | 10500
SB-002 | 150 | S.S | PUDDLE PIPE O.A 1100mm. BOTH ENDS FLANGED WITH PUDDLE FLANGE 440mm FROM ONE END. WITH 50mm TAP OFF. |  | 1 | 15000 | 15000
SB-003 | 350 | S.S | PUDDLE PIPE 0.A 2400mm. ONE END FLANGED WITH PUDDLE FLANGE 465mm FROM FLAGED END. |  | 1 | 30000 | 30000
SB-004 | 150 | S.S | PUBBLE PIPE 0.A 955mm. BOTH ENDS PLAIN WITH PUDDLE FLANGED 705mm FROM END. |  | 2 |  | 0
SB-005 | 150 |  | FLANGED ADAPTOR |  | 2
V-001 | 150 |  | FLANGED WEDGE GATE VALVE |  | 2 | 50000 | 100000
V-002 | 50 |  | BALL VALVE |  | 1 | 3000 | 3000
SUB-TOTAL CARRIED FORWARD | [6 empty] | 55500
|  | brought forward |  |  |  |  | 55500
VALVE BUILDING
VB-001 | 600 | S.S | PUDDLE PIPE O.A 900mm BOTH ENDS FLANGED WITH PUDDLE FLANGE 450mm FROM ONE END. |  | 2 | 85000 | 170000
VB-002 | 600 | S.S | STANDARD FLANGED 90° Y-PIECE, BRANCH 1265mm C TO F. 50mm TAP OFF 320mm FROM FLANGED END |  | 1
VB-003 | 600 | S.S | STANDARD D.F 45° SHORT RADIUS BEND, 610mm C TO F. |  | 4 | 75000 | 300000
VB-004 | 600 | S.S | FLANGED PIPE O.A 730mm |  | 2
VB-005 | 600 | S.S | FLANGE ADAPTOR |  | 2 | 25000 | 50000
VB-006 | 600 | S.S | UN-EQUAL TEE TWO BRANCHES 610mm C. TO F. PLAIN BRANCH 2950mm O.A 3560mm. |  | 2 | 110000 | 220000
VB-007 | 100X 600 | S.S | FLANGED 100⌀ PIPE O.A 335mm. ONE END WITH 600⌀ FLANGE |  | 2
VB-008 | 600 | S.S | STANDARD FLANGED 90°Y-PIECE BRANCHS 1265 mm C TO F |  | 1 | 125000 | 125000
VB-009 | 150 | S.S | FLANGED PIPE O.A. 1940mm |  | 1
VB-010 | 500 | S.S | PUDDLE PIP O.A 900mm. BOTH ENDS FLANGED WITH PUDDLE FLANGE 450mm FROM ONE END. |  | 2 | 50000 | 100000
VB-011 | 500 | S.S | STANDARD FLANGED 90° Y-PIECE, BRANCH'S 1100mm C. TO F. 50mm TAP OFF 300mm FROM FLANGED END. |  | 1 | 85000 | 85000
SUB-TOTAL CARRIED FORWARD | [6 empty] | 1105500
|  | brought forward |  |  |  |  | 1105500
VALVE BUILDING
VB-012 | 500 | S.S | STANDARD D.F 45° SHORT RADIUS BEND 510mm C. TO F. |  | 4 | 48000 | 192000
VB-013 | 500X300 | S.S | FLANGED ECCENTRIC REDUCER O.A 1110mm |  | 2
VB-014 | 300 |  | FLANGE ADAPTOR |  | 4 | 10000 | 40000
VB-015 | 300 | S.S | PIPE ONE END FLANGED O.A 800mm |  | 2
VB-016 | 300 | S.S | FLANGED PIPE 0.A. 2000mm. |  | 2
VB-017 | 500 | S.S | STANDARD FLANGED 90° Y-PIECE, BRANCH'S 1100mm C. TO F. 50mm TAP OFF 300mm FROM FLANGED END TOP AND BOTTOM OF Y-PIECE |  | 1
V-005 | 600 |  | ACTUATED FLANGED WEDGE GATE VALVE |  | 2 | 350000 | 700000
V-006 | 100 |  | FLANGED BALL VALVE |  | 2 | 6000 | 12000
V-007 | 100 |  | AIR RELEASE VALVE | X | 2 | 100000 | 200000
V-008 | 600 |  | NON-RETURN VALVE |  | 2 | 455000 | 910000
V-009 | 300 |  | GEARED FLANGED WEDGE GATE VALVE |  | 2 | 100000 | 200000
V-010 | 300 |  | HYTROL VALVE | X | 2
V-011 | 300 |  | INLINE STRAINER | X | 2 | 50000 | 100000
SUB-TOTAL CARRIED FORWARD | [6 empty] | 3459500
|  | brought forward |  |  |  |  | 3459500
VALVE BUILDING
V-012 | 50 |  | THREADED BALL VALVE |  | 2 | 3000 | 6000
V-013 | 50 |  | AIR RELEASE VALVE | X | 2
SUB-TOTAL CARRIED FORWARD | [6 empty] | 3465500
|  | brought forward |  |  |  |  | 3465500
DRAIN PIPING
DR-001 | 150 | S.S | FLANGED 90° SHORT RADIUS BEND. ONE END 230mm C. TO F. OTHER END PLAIN 3620mm O.A WITH PUDDLE FLANGE 125mm FROM PLAIN END |  | 1
DR-002 | 150 | S.S | FLANGED PIPE O.A 2950mm |  | 1
DR-003 | 150 | S.S | FLANGED 45° MEDIUM RADIUS BEND 230mm C. TO F. |  | 1
DR-004 | 150 | S.S | FLANGED PIPE 0.A 6000mm |  | 2 | 60000 | 120000
DR-005 | 150 | S.S | FLANGED PIPE O.A 5430mm |  | 1
INLET FLOW METER CHAMBER
IFC-001 | 500 | S.S | PUDDLE PIPE O.A. 900mm. BOTH ENDS FLANGED WITH PUDDLE FLANGE 450mm FROM ONE END. |  | 2 | 55000 | 110000
SUB-TOTAL CARRIED FORWARD | [6 empty] | 10626500
|  | brought forward |  |  |  |  | 10626500
INLET FLOW METER CHAMBER
IFC-002 | 500 | S.S | FLANGED PIPE O.A. 2100mm |  | 1
IFC-003 | 500 |  | FLANGE ADAPTOR |  | 1 | 20000 | 20000
V-003 | 500 |  | CLAMP ON FLOW METER | X | 1
OUTLET FLOW METER CHAMBER
OFC-001 | 500 | S.S | PUDDLE PIPE O.A 900mm. BOTH ENDS FLANGED WITH PUDDLE FLANGE 450mm FROM ONE END. |  | 2
OFC-002 | 500 | S.S | PIPE ONE END FLANGED O.A 2100mm |  | 1
OFC-003 | 500 |  | FLANGE ADAPTOR |  | 1
V-004 | 500 |  | CLAMP ON FLOW METER | X | 1
INLET PIPING
IP-001 | 500 | COATED M.S. | FLANGED PIPE O.A 600mm |  | 13 | 60000 | 780000
IP-002 | 500 | COATED M.S. | PIPE PME EMD FLANGED O.A 4400mm |  | 1
IP-003 | 500 | COATED M.S. | FLANGED PIPE O.A 5000mm |  | 1
IP-004 | 500 | COATED M.S. | FLANGED PIPE O.A 3200mm |  | 1 | 50000 | 50000
SUB-TOTAL CARRIED FORWARD | [6 empty] | 11476500
|  | brought forward |  |  |  |  | 11476500
INLET PIPING
IP-005 | 500 | COATED M.S. | FLANGED PIPE O.A 1100mm |  | 1 | 35000 | 35000
IP-006 | 500 | COATED M.S. | FLANGED PIPE O.A 185mm |  | 1
IP-006 | 500 | COATED M.S. | FLANGED PIPE O.A 3670mm |  | 1
IP-007 | 500 | COATED M.S. | FLANGED 90° MEDIUM RADIUS BEND. ONE END 1020mm c. TO F. OTHER END 6000mm C. TO F. |  | 1
IP-008 | 500 | COATED M.S. | FLANGED 90° SHORT RADIUS BEND. ONE END 5035mm C. TO F. OTHER END 510mm C. TO F. |  | 1 | 55000 | 55000
IP-009 | 500 | COATED M.S. | PUDDLE PIPE, PUDDLE FLANGE 690mm FROM FLANGED END WITH PLAIN EDED 90° SHORT RADIUS BEND 510mm C. TO F. |  | 1
IP-010 | 500 | COATED M.S. | FLANGED 90° MEDIUM RADIUS BEND. 1020MM C. TO F. |  | 1 | 60000 | 60000
IP-011 | 500 |  | FLANGE ADAPTOR |  | 1 | 20000 | 20000
OUTLET PIPING
OP-001 | 600 | COATED M.S | FLANGED PIPE O.A 6000mm |  | 15 | 70000 | 1050000
OP-002 | 600 | COATED M.S | PIPE ONE END FLANGED O.A 4400mm |  | 1 | 60000 | 60000
SUB-TOTAL CARRIED FORWARD | [6 empty] | 12756500
|  | brought forward |  |  |  |  | 12756500
OP-003 | 600 | COATED M.S | FLANGED PIPE O.A 3190mm |  | 1 | 50000 | 50000
OP-004 | 600 | COATED M.S | FLANGED PIPE O.A 4440mm |  | 1 | 60000 | 60000
OP-005 | 600 | COATED M.S | FLANGED PIPE O.A 3580mm |  | 1
OP-006 | 600 | COATED M.S | FLANGED 90° MEDIUM RADIUS BEND. ONE END 1020mm C. TO F. OTHER END WITH BELLMOUTH O.A 3695mm |  | 1 |  | 0
OP-007 | 600 | COATED M.S | FLANGED 90° MEDIUM RADIUS BEND. 1020mm C. TO F. |  | 1 | 45000 | 45000
OP-008 | 600 |  | FLANGE ADAPTOR |  | 1 | 25000 | 25000
TOTAL FOR SECTION 6 (Carried to Summary) | [6 empty] | 12936500
Note on F86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2
Note on C209: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: LC BOQ - EPOXY MILD STEEL

## Pipe Schedule
PIPE SCHEDULE
Mark on dwg | NB (mm) | Mat | Decription | Sketch | No. | Rate | Amount
SECTION 4: RESERVOIR
OVERFLOW PIPING
OF-001 | 350 | SS 304 3mm w.t. | FLANGED BELLMOUTH, O.A. 6000mm, BELLMOUTH 550mm DIA. |  | 1 |  | 0
OF-002 | 350 | SS 304 3mm w.t. | FLANGED 90° SHORT RADIUS BEND. ONE END 360mm C. to F. OTHER END 2635mm C. to F. |  | 1 |  | 0
OF-003 | 350 | SS 304 3mm w.t. | FLANGED PIPE, O.A. 2950mm |  | 1 |  | 0
SCOUR PIPING
SP-001 | 150 | SS 304 3mm w.t. | 90° SHORT RADIUS BEND ONE END 230mm C. TO F. AND FLANGED, OTHER END 960mm C. to F. WITH BELLMOUTH OD OF 245mm |  | 1 |  | 0
SP-002 | 150 | SS 304 3mm w.t. | FLANGED PIPE O.A.3200mm |  | 1 |  | 0
DRAIN PIPING
DR-001 | 150 | SS 304 3mm w.t. | FLANGED 90° SHORT RADIUS BEND. ONE END 230mm C. TO F. OTHER END PLAIN 395mm O.A.WITH PUDDLE FLANGE 100mm FROM PLAIN END |  | 1 |  | 0
DR-002 | 150 | SS 304 3mm w.t. | FLANGED PIPE 0.A 6000mm |  | 2 |  | 0
DR-003 | 150 | SS 304 3mm w.t. | FLANGED PIPE 0.A 4380mm |  | 1 |  | 0
DR-004 | 150 | SS 304 3mm w.t. | FLANGED 24° MEDIUM RADIUS BEND 230mm C. to F. |  | 1 |  | 0
DR-005 | 150 | SS 304 3mm w.t. | FLANGED PIPE O.A.5430mm |  | 1 |  | 0
TOTAL CARRIED TO ITEM 4.2.1 | [6 empty] | 0
SECTION 5: CHAMBERS AND BOXES
SCOUR BOX
SB-001 | 150 | SS 304 3mm w.t. | PUDDLE PIPE O.A.1300mm. BOTH ENDS FLANGED WITH PUDDLE FLANGE 650mm FROM ONE END. |  | 1
SB-002 | 150 | SS 304 3mm w.t. | PUDDLE PIPE O.A.1300mm. BOTH ENDS FLANGED WITH P.F. 650mm FROM ONE END AND 50mm BOSS 250mm FROM OTHER END |  | 1
SB-003 | 350 | SS 304 3mm w.t. | PUDDLE PIPE 0.A 2600mm. ONE END FLANGED WITH PUDDLE FLANGE 650mm FROM FLAGED END. |  | 1
SB-004 | 150 | SS 304 3mm w.t. | PUDDLE PIPE 0.A 1020mm. BOTH ENDS PLAIN WITH PUDDLE FLANGED 250mm FROM END. |  | 2
SB-005 | 150 | Coated M.S. | FLANGED ADAPTOR |  | 2
V-001 | 150 | D.I. | WEDGE GATE VALVE, PN10, NON RISING SPINDLE, CLOCKWISE CLOSING, COMPLETE WITH HANDWHEEL, DUCTILE IRON BODY AND COVER, STAINLESS STEEL SPINDLE, "O" RING GLAND SEAL ARRANGEMENT, PINNED GUNMETAL SEATS |  | 2
V-002 | 50 | SS 304 | THREADED BALL VALVE |  | 1
TOTAL CARRIED TO ITEM 5.1.6.1
INLET FLOW METER CHAMBER
IFC-001 | 500 | SS 304 4mm w.t. | PUDDLE PIPE O.A. 1300mm. BOTH ENDS FLANGED WITH PUDDLE FLANGE 650mm FROM ONE END. |  | 2
IFC-002 | 500 | SS 304 3mm w.t. | FLANGED PIPE O.A. 2100mm |  | 1
IFC-003 | 500 | Coated M.S. | FLANGE ADAPTOR |  | 1
TOTAL CARRIED TO ITEM 5.2.6.1
OUTLET FLOW METER CHAMBER
OFC-001 | 500 | SS 304 4mm w.t. | PUDDLE PIPE O.A.1300mm. BOTH ENDS FLANGED WITH PUDDLE FLANGE 650mm FROM ONE END. |  | 2
OFC-002 | 500 | SS 304 4mm w.t. | PIPE O.A.2100mm, ONE END FLANGED OTHER END PLAIN |  | 1
OFC-003 | 500 | Coated M.S. | FLANGE ADAPTOR |  | 1
TOTAL CARRIED TO ITEM 5.3.6.1
VALVE CHAMBERS
VC-001 | 500 | SS 304 4mm w.t. | PUDDLE PIPE O.A.1300mm. BOTH ENDS FLANGED WITH PUDDLE FLANGE 650mm FROM ONE END. |  | 3
VC-002 | 500 | SS 304 4mm w.t. | UN-EQUAL TEE, PLAIN ENDED BRANCH 810mm C. to F. 850mm C. to F. FROM FLANGED END, OTHER END PLAIN 715mm C. to F. |  | 1
VC-003 | 500 | Coated M.S. | FLANGE ADAPTOR |  | 2
VC-004 | 500 | D.I. | WAFER TYPE KNIFE GATE VALVE WITH STAINLESS STEEL BLADE AND SPINDLE, PN10, O.A. 100mm |  | 2
VC-005 | 600 | SS 304 5mm w.t. | PUDDLE PIPE O.A.1300mm. BOTH ENDS FLANGED WITH PUDDLE FLANGE 650mm FROM ONE END. |  | 3
VC-006 | 600 | SS 304 5mm w.t. | UN-EQUAL TEE, PLAIN ENDED BRANCH 800mm C. to F. 850mm C. to F. FROM FLANGED END, OTHER END PLAIN 700mm C. to F. |  | 1
VC-007 | 600 | Coated M.S. | FLANGE ADAPTOR |  | 2
VC-008 | 600 | D.I. | WAFER TYPE KNIFE GATE VALVE WITH STAINLESS STEEL BLADE AND SPINDLE, PN10, O.A. 110mm |  | 2
TOTAL CARRIED TO ITEM 5.5.6.1
SECTION 6: INTERCONNECTING PIPEWORK
INLET PIPING
IP-001 | 500 | Coated M.S. 5mm w.t. | FLANGED PIPE O.A.600mm |  | 9
IP-002 | 500 | Coated M.S. 5mm w.t. | PIPE PME EMD FLANGED O.A.6000mm |  | 1
IP-003 | 500 | Coated M.S. | FLANGE ADAPTOR |  | 1
IP-004 | 500 | Coated M.S. 5mm w.t. | FLANGED PIPE O.A.3850mm |  | 1
IP-005 | 500 | Coated M.S. 5mm w.t. | FLANGED PIPE O.A.3000mm |  | 1
IP-006 | 500 | Coated M.S. 5mm w.t. | FLANGED PIPE O.A.4950mm |  | 1
IP-007 | 500 | Coated M.S. 5mm w.t. | FLANGED PIPE O.A.1450mm |  | 1
IP-008 | 500 | Coated M.S. 5mm w.t. | FLANGED 90° MEDIUM RADIUS BEND. ONE END 1020mm c. TO F. OTHER END 4100mm C. TO F. |  | 1
IP-009 | 500 | Coated M.S. 5mm w.t. | FLANGED 90° SHORT RADIUS BEND. ONE END 5035mm C. TO F. OTHER END 510mm C. TO F. |  | 1
IP-010 | 500 | SS 304 4mm w.t. | UNEQUAL 90° SHORT RADIUS BEND, ONE END PLAIN 510mm C. to F. OTHER END FLANGED 1510 C. to F. WITH P.F. 690mm FROM FLANGED END |  | 1
TOTAL CARRIED TO ITEM 6.2.5
OUTLET PIPING
OP-001 | 600 | Coated M.S. 6mm w.t. | FLANGED PIPE O.A.6000mm |  | 8
OP-002 | 600 | Coated M.S. 6mm w.t. | PIPE ONE END FLANGED O.A.5300mm |  | 1
OP-003 | 600 | Coated M.S. | FLANGE ADAPTOR |  | 1
OP-004 | 600 | Coated M.S. 6mm w.t. | FLANGED PIPE O.A.5150mm |  | 1
OP-005 | 600 | Coated M.S. 6mm w.t. | FLANGED PIPE O.A.3000mm |  | 1
OP-006 | 600 | Coated M.S. 6mm w.t. | FLANGED PIPE O.A.5100mm |  | 1
OP-007 | 600 | SS 304 5mm w.t. | UNEQUAL 90° MEDIUM RADIUS BEND, ONE END FLANGED 2715mm C. to F. OTHER END WITH BELLMOUTH 1790mm C. to F. |  | 1
TOTAL CARRIED TO ITEM 6.2.6
SECTION 9: VALVE BUILDING
VALVE BUILDING
VB-001 | 600 | SS 304 5mm w.t. | PUDDLE PIPE O.A.900mm BOTH ENDS FLANGED WITH PUDDLE FLANGE 450mm FROM ONE END. |  | 2
VB-002 | 600 | Coated M.S. 6mm w.t. | FLANGED 90° Y-PIECE, BRANCHES 1265mm C to F. MAIN PIPE 320mm C. to F. WITH 50mm BOSS 320mm FROM MAIN FLANGED END |  | 1
VB-003 | 600 | Coated M.S. 6mm w.t. | STANDARD D.F 45° SHORT RADIUS BEND, 610mm C TO F. |  | 4
VB-004 | 600 | Coated M.S. 6mm w.t. | FLANGED PIPE O.A.730mm WITH 25mm BOSS 250mm FROM ONE END. |  | 2
VB-005 | 600 | Coated M.S. | FLANGE ADAPTOR |  | 2
VB-006 | 600 | Coated M.S. 6mm w.t. | UN-EQUAL TEE, ONE END FLANGED 610mm C.to F. OTHER END PLAIN 2790mm C. to F. WITH FLANGED ENDED BRANCH 610mm C. to F. |  | 2
VB-007 | 100X 600 | Coated M.S. | 600⌀ BLANK FLANGE DRILLED FOR 100⌀ PIPE O.A.335mm WITH FLANGED END |  | 2
VB-008 | 600 | Coated M.S. 6mm w.t. | FLANGED 90° Y-PIECE, BRANCHES 1265mm C to F. MAIN PIPE 320mm C. to F. |  | 1
VB-009 | 600 | Coated M.S. 6mm w.t. | FLANGED PIPE O.A. 1940mm |  | 1
VB-010 | 500 | SS 304 4mm w.t. | D.F. PUDDLE PIPE O.A.1300mm. WITH P.F. 650mm FROM ONE END. |  | 2
SUB-TOTAL CARRIED FORWARD
brought forward
VALVE BUILDING (CONTINUED)
VB-011 | 500 | Coated M.S. 5mm w.t. | FLANGED 90° Y-PIECE, BRANCHES 1100mm C. to F. MAIN PIPE 300mm C. to F. WITH 50mm BOSS 300mm FROM FLANGED END. |  | 1
VB-012 | 500 | Coated M.S. 5mm w.t. | STANDARD D.F 45° SHORT RADIUS BEND 510mm C. TO F. |  | 4
VB-013 | 500X 300 | Coated M.S. 4mm w.t. | FLANGED ECCENTRIC 500mm to 300mm REDUCER AND 300mm DIA. PIPE O.A.1110mm |  | 2
VB-014 | 300 | Coated M.S. | FLANGE ADAPTOR |  | 4
VB-015 | 300 | Coated M.S. 4mm w.t. | PIPE ONE END FLANGED O.A.800mm |  | 2
VB-016 | 300 | Coated M.S. 4mm w.t. | PIPE ONE END FLANGED 0.A. 2000mm. |  | 2
VB-017 | 500 | Coated M.S. 5mm w.t. | FLANGED 90° Y-PIECE, BRANCHES 1100mm C. to F. MAIN PIPE 300mm C. to F. WITH 50mm THREADED ENDED BOSS 300mm FROM FLANGED END AT THE BOTTOM AND A 100mm DIA. FLANGED ENDED BOSS AT THE TOP. |  | 1
V-005 | 600 | D.I. | WEDGE GATE VALVE, PN10, NON RISING SPINDLE, CLOCKWISE CLOSING, GEARBOX OPERATED COMPLETE WITH HANDWHEEL, DUCTILE IRON BODY AND COVER, STAINLESS STEEL SPINDLE, "O" RING GLAND SEAL ARRANGEMENT, PINNED GUNMETAL SEATS, O.A. 600mm |  | 2
V-006 | 100 | SS 304 | FLANGED BALL VALVE |  | 2
V-007 | 100 | SS 304 | DOUBLE ORIFICE AIR RELEASE AND VACUUM BREAKER VALVE WITH ANTI SHOCK MECHANISM |  | 2
SUB-TOTAL CARRIED FORWARD
brought forward
VALVE BUILDING (CONTINUED)
V-008 | 600 | D.I. | FLANGED TILITING DISC NON-RETURN VALVE |  | 2
V-009 | 300 | D.I. | WEDGE GATE VALVE, PN10, NON RISING SPINDLE, CLOCKWISE CLOSING, GEARBOX OPERATED COMPLETE WITH HANDWHEEL, DUCTILE IRON BODY AND COVER, STAINLESS STEEL SPINDLE, "O" RING GLAND SEAL ARRANGEMENT, PINNED GUNMETAL SEATS, O.A. 380MM |  | 4
V-010 | 300 | D.I. | HYDRAULIC CONTROL VALVE INCLUDING 20mm SS BI-LEVEL CONTROL PILOT INSIDE RESERVOIR WITH 15mm SS CONNECTION PIE |  | 2
V-011 | 300 | Coated M.S. 4mm w.t. | FLANGED BASKET STRAINER, O.A. 800mm |  | 2
V-012 | 50 | SS 304 | THREADED BALL VALVE |  | 2
V-013 | 50 | SS 304 | DOUBLE ORIFICE AIR RELEASE AND VACUUM BREAKER VALVE WITH ANTI SHOCK MECHANISM |  | 1
V-014 | 600 | D.I. | WAFER TYE KNIFE GATE VALVE, PN 10, STAINLESS STEEL BLADE AND SPLINDLE, O.A 110mm. |  | 4
V-015 | 300 | D.I. | WAFER TYPE KNIFE GATE VALVE, PN 10, STAINLESS STEEL BLADE AND SPINDLE, O.A. 70mm |  | 4
V-016 | 25 | SS 304 | THREADED BALL VALVE |  | 2
TOTAL CARRIED TO ITEM 9.1.10

## 1. P&G
SECTION 1: PRELIMINARY AND GENERAL
ITEM NO | PAYMENT CLAUSE | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
| SANS 1200A | SECTION 1: PRELIMINARY & GENERAL
1.1 | 8.3 | FIXED CHARGE AND VALUE RELATED ITEMS
| 8.3.1 | Contractual Requirements
1.1.1 |  | Surety or Bank Guarantee | Sum | 1
1.1.2 |  | Insurance of Works | Sum | 1
1.1.3 |  | Common Law Liability Insurance | Sum | 1
1.1.4 |  | Third Party Insurance | Sum | 1
1.1.5 |  | Insurance of Construction Plant and Equipment | Sum | 1
1.1.6 | PSA 8.3.1 | Initial Insurance Deductible | Sum | 1
1.1.7a |  | Any Other Insurances that the Tenderer deems necessary to comply with Insurance requirements (Detail …………………………………………………........…....……........) | Sum | 1
1.1.7b |  | Other (Detail …………………………………………………....……........) | Sum | 1
Forward Cover
1.1.8 | PS 6.18 | In respect of the total value of imported content of goods used in the reservoir from page RD30 Imported Content Sheet R ….........................................
1.1.9 |  | Allow a Provisional Sum to cover variation in exchange rate prior to obtaining forward cover. Tenderer is to insert an amount = 20% of the above amount from Item 1.1.8 | Prov. Sum | 1
1.1.10 |  | Allow a Provisional Sum to cover the cost of forward cover Tenderer is to insert an amount = 10% of the above amount from item 1.1.8 | Prov. Sum | 1
1.1.11 |  | Allowance as a percentage of the PC value of items under 1.1.9 and 1.1.10 for Contractor's cost and profit. Tenderer to insert the summed amount (calculated under 1.1.9 and 1.1.10) in the "Qty" column, and state percentage in the "Rate" column. | %
| 8.3.2 | Establish Facilities on the Site |  |  |  |  | >> Check PSAB in Specs
| 8.3.2.1 | Facilities for the Employer's Agent
1.1.12 | PS 5.6.1 | (a) Offices (3 no. off) | Sum | 1
1.1.13 |  | (c) Nameboards | Sum | 2
1.1.14 | PSA 8.3.2.1 | (d) Latrine facilities | Sum | 1
1.1.15 | PSA 8.3.2.1 | (e) Boardroom to accommodate 15 people | Sum | 1
1.1.16 | PSA 8.3.2.1 | (f) Carports (5 off) | Sum | 1
1.1.17 | PSA 8.3.2.1 | (h) Construction and setting out of survey beacons, including beacons to confirm property boundaries | No. | 8
1.1.18 | PSA 8.3.2.1 | (i) Furniture for offices and meeting rooms | Sum | 1
1.1.19 | PSA 8.3.2.1 | (j) Laptop, Data and Software | Sum | 1
| 8.3.2.2 | Facilities for the Contractor
1.1.20 |  | (a) Offices and Storage Sheds | Sum | 1
SUB-TOTAL CARRIED FORWARD
brought forward
1.1.21 |  | (b) Workshops | Sum | 1
1.1.22 |  | (c) Laboratories | Sum | 1
1.1.23 |  | (e) Ablution and Latrine Facilities | Sum | 1
1.1.24 | PSA 8.3.2.2 | (f) Tools and Equipment | Sum | 1
1.1.25 |  | (g) Water Supplies, Electric Power & Communications | Sum | 1
1.1.26 |  | (h) Dealing with Water | Sum | 1
1.1.27 |  | (i) Access | Sum | 1
1.1.28 |  | (j) Plant | Sum | 1
1.1.29 | PSA 8.3.2.2 | (k) Security of the works | Sum | 1
1.1.30 | PSA 8.3.2.2 | (l) Personal protection equipment | Sum | 1
1.1.31 | 8.3.3 | Other Fixed Charge Obligations | Sum | 1
1.1.32 | 8.3.4 | Removal of Site Establishment | Sum | 1
1.1.33 |  | Compliance with the Occupational Health and Safety Act and Specification (Including compliance with COVID-19 Regulations) | Sum | 1
1.1.34 |  | Compliance with the Environmental Management Plan and Vegetation Management Plan | Sum | 1
1.1.35 |  | Hazard Identification and Risk Assessment | Sum | 1
1.1.36 |  | Construction Safety Officer and Other Appointments | Sum | 1
1.1.37 |  | Work Skills Plan and Implementation Report to CETA | Sum | 1
1.1.38 |  | Pre-Employment Medical Examinations | Sum | 1
1.2 | 8.4 | TIME RELATED ITEMS
| 8.4.1 | Contractual Requirements
1.2.1 |  | Surety or Bank Guarantee | Sum | 1
1.2.2 |  | Insurance of Works | Sum | 1
1.2.3 |  | Common Law Liability Insurance | Sum | 1
1.2.4 |  | Third Party Insurance | Sum | 1
1.2.5 |  | Insurance of construction plant and equipment | Sum | 1
1.2.6a |  | Any Other Insurances that the Tenderer deems necessary to comply with Insurance requirements (Detail …………………………………………………........…....……........) | Sum | 1
1.2.6b |  | Other (Detail …………………………………………...........…..…….) | Sum | 1
| 8.4.2 | Operation and Maintenance of facilities on site, for the duration of construction, except where otherwise stated
| 8.4.2.1 | Facilities for Employer's Agent for the Duration of Construction
1.2.7 |  | (a) Furnished offices (3 no. off.) | Sum | 1
1.2.8 |  | (c) Nameboards | Sum | 1
SUB-TOTAL CARRIED FORWARD
brought forward
1.2.9 | PSA 8.4.2.1 | (e) Latrine facilities for the sole use of the Employer's Agent | Sum | 1
1.2.10 | PSA 8.4.2.1 | (f) Boadroom to accommodate 15 personnel | Sum | 1
1.2.11 | PSA 8.4.2.1 | (g) Carports (5 off) | No. | 5
1.2.12 | PSA 8.4.2.1 | (h) Construction and setting out of survey beacons | No. | 8
1.2.13 | PSA 8.4.2.1 | (i) Furniture for offices and meeting rooms | Sum | 1
1.2.14 |  | (j) Laptop, Data and Software | Sum | 1
| 8.4.2.2 | Facilities for the Contractor
1.2.15 |  | (a) Offices and Storage Sheds | Sum | 1
1.2.16 |  | (b) Workshops | Sum | 1
1.2.17 |  | (c) Laboratories | Sum | 1
1.2.18 |  | (e) Ablution and Latrine Facilities | Sum | 1
1.2.19 |  | (f) Tools and Equipment | Sum | 1
1.2.20 |  | (g) Water supplies, electricpower and communications, dealing with water and access | Sum | 1
1.2.21 |  | (h) Dealing with water | Sum | 1
1.2.22 |  | (i) Access | Sum | 1
1.2.23 |  | (j) Plant | Sum | 1
1.2.24 | PSA 8.4.2.2 | (k) Security of the works | Sum | 1
1.2.25 | PSA 8.4.2.2 | (l) Water tanker for dust suppression | Sum | 1
1.2.26 | PSA 8.4.3 | Supervision for the duration of the Contract | Sum | 1
1.2.27 | 8.4.4 | Company and head office overhead costs for the duration of the contract | Sum | 1
1.2.28 |  | Compliance with the Occupational Health and Safety Act and Specification (Including compliance with COVID-19 Regulations) | Sum | 1
1.2.29 |  | Compliance with the Environmental Management Plan and Vegetation Management Plan | Sum | 1
1.2.30 |  | Construction Safety Officer and Other Appointments | Sum | 1
1.2.31 |  | Work Skills Plan and Implementation Report to CETA | Sum | 1
1.2.32 |  | Compliance with contractual reporting requirements and managing of processes for local content | Sum | 1
1.2.33 | 8.4.5 | Other time-related obligations
|  | ….......................... | Sum | 1
1.3 | PSA 8.5 | SUMS STATED PROVISIONALLY BY THE EMPLOYER'S AGENT
1.3.1 | (b) (3) | (a) Provisional sum for control testing to be carried out as required by the Employer's Agent including testing of the structure | Prov. Sum | 1 | 100000 | 100000
1.3.2 |  | (b) Additional tests ordered by the Employer's Agent | Prov. Sum | 1 | 50000 | 50000
1.3.3 |  | (c) Community Liaison Officer (CLO) | Prov.Sum | 1 | 255000 | 255000 | >> Check PSAB
1.3.4 |  | (d) Training of targetted labour and SMME's | Prov.Sum | 1 | 1000000 | 1000000 | >> Check PSAB
1.3.5 |  | (e) Skills Development and Training | Prov.Sum | 1 | 864000 | 864000 | >> Check PSAB
1.3.6 |  | (f) Signage for buildings | Prov.Sum | 1 | 50000 | 50000
1.3.7 |  | (g) GPR survey | Prov.Sum | 1 | 100000 | 100000
SUB-TOTAL CARRIED FORWARD
brought forward
1.3.8 |  | (h) Protection of existing services | Prov.Sum | 1 | 150000 | 150000
1.3.9 |  | (i) Application for Environmental regulation | Prov.Sum | 1 | 50000 | 50000
1.3.10 |  | (j) Environmental Control Officer | Prov.Sum | 1 | 144000 | 144000
1.3.11 |  | (k) Full time Environmental Liaison Officer | Prov.Sum | 1 | 720000 | 720000
1.3.12 |  | (l) Project Mentor or support services for the Contractor or for Sub-contractors, SMME's, etc. | Prov.Sum | 1 | 3660000 | 3660000
1.3.13 |  | (m) Contractor's percentage to cover cost of handling for items 1.3.1 to 1.3.12 | % | 7143000
1.4 | 8.7 | DAYWORK
1.4.1 | PSA 8.7.1 | Expenditure on dayworks | Prov.Sum | 1 | 200000 | 200000
| PSA 8.7.2 | Extra over item 1.4.1 for supervision, overheads and all other costs related to the Daywork items under item 1.4.2 to 1.4.4 for the following:
1.4.2 |  | (a) Skilled labourers | % | 75000
1.4.3 |  | (b) Unskilled labourers | % | 75000
1.4.4 |  | (c) Material | % | 50000
| PS 8.7.3 | Plant Hire Rates
The appropriate types and sizes (T&S) of the plant shall be stated in the space provided:
1.4.5 |  | Mobile cranes (Type & Size ……….……………...………............…….) | hrs | 24
1.4.6 |  | Front-end loader (T&S…………....……………………………...............) | hrs | 40
1.4.7 |  | Bulldozer (T&S……………………………………………........................) | hrs | 40
1.4.8 |  | Grader (T&S…......................................................................................) | hrs | 40
1.4.9 |  | Excavators (T&S………………..………………………….......................) | hrs | 40
1.4.10 |  | Tip Trucks (T&S….................................................................................) | hrs | 40
1.4.11 |  | TLB's (T&S…........................................................................................) | hrs | 40
1.4.12 |  | Portable compressor and breakers etc. (T&S….....................................) | hrs | 40
1.4.13 |  | Portable pumps and hoses (T&S…........................................................) | hrs | 40
1.4.14 |  | Others give full details:
|  | …………………………………………………………………. | rate/hr
|  | …………………………………………………………………. | hrs only
1.5 | PSA 8.8 | TEMPORARY WORKS
1.5.1 | PSA 8.8.2 | Dealing with traffic and maintain Roads | Sum | 1
| PSA 8.8.4 | Relocation of services
1.5.2 |  | Excavation for exposing services in the following depth ranges below ground level:
(a) 0.0m up to 2.0m:
1.5.3 |  | (i) Soft material | m³ | 60
1.5.4 |  | (ii) Intermediate material | m³ | 180
1.5.5 |  | (iii) Hard material | m³ | 60
SUB-TOTAL CARRIED FORWARD
brought forward
(b) Exceeding 2.0m up 4.0m:
1.5.6 |  | (i) Soft material | m³ | 64
1.5.7 |  | (ii) Intermediate material | m³ | 192
1.5.8 |  | (iii) Hard material | m³ | 64
1.6 | PSA 8.9 | DELAYS
1.6.1 |  | Delay due to total work stoppage (the Daily rate must equal the total of the Daily Time Related P&G Cost. Only this Daily rate will be paid in the event of ANY approved delays to the Due Completion Date of the Contract) | days | 20
1.7 | PSA 8.10 | SUBCONTRACTORS (SMME's)
1.7.1 |  | Fixed-Charge items for the sub-contractors Contractual Requirements |  |  |  | Refer to Summary Page
1.7.2 | PSA 8.10.2 | Overhead, charges and profit for the Main Contractor to provide for fixed-charge items for the sub-contractors Contractual Requirements |  |  |  | Refer to Summary Page
1.7.3 |  | Time Related items for the sub-contractors Contractual Requirements |  |  |  | Refer to Summary Page
1.7.4 | PSA 8.10.3 | Overhead, charges and profit for the Main Contractor to provide for time related items for the sub-contractors Contractual Requirements |  |  |  | Refer to Summary Page
1.7.5 | PSA 8.10.4 | Provisional Sum to cover costs incurred by the Contractor when making payments of behalf of the sub-contractor (ref Contract Data) or to provide ad-hoc services on behalf of the sub-contractor | Prov.Sum | 1 | 100000 | 100000
TOTAL FOR SECTION 1 (Carried to Summary)

## Master Rates (hidden)
Master Rates |  | Concrete Factors |  | Master Rates |  | Concrete Factors
Site Clearance (per/m2) | 5
Concrete ( per m3) | 2800 | RETAINING WALLS | 1 | Concrete ( per m3) | 2750 | RETAINING WALLS | 1
Formwork ( per m2) | 755 | ACCESS ROADS AND STORMWATER | 1 | Blinding Layer | 130 | ACCESS ROADS AND STORMWATER | 1
Formwork Domed Roof ( per m2) | 1200 | HEAD OF WORKS | 1.5 | Formwork ( per m2) | 755 | HEAD OF WORKS | 1.5
Formwork Walls ( per m2) | 500 | PRIMARY TREATMENT | 1.3 | Wood Float Finish ( per m2) | 10 | PRIMARY TREATMENT | 1.3
Reinforcement Walls & Footings at 400kg/m3 ( per ton) | 18000 | FLOW BALANCING | 1.13 | Reinforcement ( per ton) | 18000 | FLOW BALANCING | 1.13
Mesh Ref 245 | 50 | BIOLOGICAL REACTOR | 1.25 | Bulk Excavation (per m3) |  | BIOLOGICAL REACTOR | 1.25
Mesh Ref 617 | 90 | SECONDARY TREATMENT | 1.3 | Soft | 120 | SECONDARY TREATMENT | 1.3
Reinforcement Columns at 120kg/m3 ( per ton) | 18000 | DISINFECTION & FINAL EFFLUENT | 1.2 | Intermediate | 250 | DISINFECTION & FINAL EFFLUENT | 1.2
|  | STORM FLOW DAM | 1 | Hard | 850 | STORM FLOW DAM | 1
Bulk Excavation (per m3) |  | FERMENTER AREA | 1.3 | Remove Top Soil | 12 | FERMENTER AREA | 1.3
Soft | 140 | ANCILLARY WORKS | 1.37 | Restricted Excavation (per m3) |  | ANCILLARY WORKS | 1.37
Intermediate | 190 | INTERCONNECTING PIPEWORK | 1.37 | Soft | 210 | INTERCONNECTING PIPEWORK | 1.37
Hard | 985 |  |  | Intermediate | 375
|  |  |  | Hard | 1182
Restricted Excavation (per m3) |  | Pipelines |  | Allowance for Mass Concrete | 5% | Pipelines
Soft | 210 | Description | Rate (R/m) | Contingency by the Engineer | 0% | Description | Rate (R/m)
Intermediate | 375 | Concrete Pipelines |  | Buildings Engineering (R/m²) | 6500 | Concrete Pipelines
Hard | 1182 | Class 100D Diameter 500 Concrete Pipe | 1300 | Building Architectural (R/m²) | 10000 | Class 100D Diameter 450 Concrete Pipe | 677
Allowance for Mass Concrete | 0.05 | Class 100D Diameter 750 Concrete Pipe | 1900 | Restricted Excavation | 100% | Class 100D Diameter 600 Concrete Pipe | 1056
Contingency by the Engineer | 0 | Class 100D Diameter 900 Concrete Pipe | 2500 | Soft | 55% | Class 100D Diameter 750 Concrete Pipe | 1600
Buildings Engineering (R/m²) | 10000 | Class 100D Diameter 1000 Concrete Pipe | 3500 | Intermediate | 22.5% | Class 100D Diameter 900 Concrete Pipe | 2100
Building Architectural (R/m²) | 12000 | Class 100D Diameter 1200 Concrete Pipe | 4700 | Hard | 22.5% | Class 100D Diameter 1000 Concrete Pipe | 3000
Restricted Excavation | 1 | Class 100D Diameter 1500 Concrete Pipe | 6660 | Bulk Excavation | 100% | Class 100D Diameter 1200 Concrete Pipe | 4000
Soft | 20% | Class 100D Diameter 1800 Concrete Pipe | 9300 | Soft | 90% | Class 100D Diameter 1500 Concrete Pipe | 5750
Intermediate | 20% |  |  | Intermediate | 10% | Class 100D Diameter 1800 Concrete Pipe | 8000
Hard | 60% | HDPE Pipelines |  | Hard | 0%
Bulk Excavation | 100% | PN12.5 Diameter 160 HDPE Pipe | 530 | Bulk Excavation & dispose (per m3) | 120 | HDPE Pipelines
Soft | 20% | PN12.5 Diameter 500 HDPE Pipe | 1800 | Bulk Excavation & Reuse (per m3) | 200 | PN12.5 Diameter 160 HDPE Pipe | 450
Intermediate | 20% |  |  | Dispose | 10% | PN12.5 Diameter 500 HDPE Pipe | 1500
Hard | 60% | Stainless Steel Pipes |  | Reuse | 90%
Bulk Excavation & dispose (per m3) | 140 | SS304 Diamter 150 Pipe | 1400 | Import G7 fill material | 250 | Stainless Steel Pipes
Dispose | 10% | SS304 Diamter 350 Pipe | 4650 | Import G5 fill material | 260 | SS304 Diamter 200 Pipe | 1200
Reuse | 90% | SS304 Diamter 450 Pipe | 6220 | 80 mm Interlocking Paving Blocks (per m²) | 200 | SS304 Diamter 500 Pipe | 6000
Import G7 fill material | 205 | SS304 Diamter 500 Pipe | 7000 | 60 mm Interlocking Paving Blocks (per m²) | 150 | SS304 Diamter 900 Pipe | 10000
80 mm Interlocking Paving Blocks (per m²) | 235 | SS304 Diamter 600 Pipe | 8000 | 150 mm C4 (per m³) | 250 | SS304 Diamter 1000 Pipe | 12000
60 mm Interlocking Paving Blocks (per m²) | 175 | SS304 Diamter 800 Pipe | 10000 | 150 mm rip and recompact (per m³) | 120
150 mm C4 (per m³) | 290 | SS304 Diamter 1000 Pipe | 14000 | Precast kerbing units (per m) | 250 | uPVC Pipes
150 mm rip and recompact (per m³) | 140 | SS304 Diamter 1200 Pipe | 20000 | Manholes with Concrete Cover (per 1 no. off) | 6015 | Diameter 200 Class 12 | 300
Precast kerbing units (per m) | 290 |  |  | Kerb Inlets (per 1 no. off) | 8000 | Diameter 110 | 122
Manholes (per 1 no. off) | 7530 | uPVC Pipes |  | Manholes with Grid Inlet (per 1 no. off) | 9716
Kerb Inlets (per 1 no. off) | 9300 | Diameter 50 Class 12 | 150 | Culverts (per 1 no. off) | 6500 | Weholite Pipes
Grid Inlets (per m) | 2320 | Diameter 75 Class 12 | 180 |  |  | Diameter 450 | 1288
Culverts (per 1 no. off) | 7525 | Diameter 110 Class 12 | 210 | Emergency Dam (R/m³) | 750 | Diameter 1500 | 10640
|  | Diameter 200 Class 12 | 350 | P & G (%) | 20% | Diameter 1800 | 15528
Emergency Dam (R/m³) | 870
P & G (%) | 0.2 | Weholite Pipes |  | Double Brickwork (per m2) | 650 | Cutting & Trimming Concrete Pipes
|  | Diameter 450 | 1500 | Single Brickwork (per m2) | 370 | Diameter 450 | 300
Brickwork (per m2) | 1195 | Diameter 1500 | 12320 | D1-Single steel door | 3000 | Diameter 600 | 400
D1-Single steel door | 3000 | Diameter 1800 | 18000 | D2-Single steel door | 2500
D2-Single steel door | 2500 |  |  | W1-Window | 850 | Pipe Trenches: 300mm - 600mm Dia Pipes
W1-Window | 850 | HDPE Pipes |  | W2-Window | 500 | 0-1m | 80
W2-Window | 500 | Diameter 50 slotted drainage pipe | 170 | Water Closet | 2000 | 1-2m | 190
Water Closet | 1500 | Diameter 75 slotted drainage pipe | 200 | Sink | 1500 | 2-3m | 310
Sink | 1000 | Diameter 110 slotted drainage pipe | 250
|  |  |  | Fencing(R/m) | 2370 | Pipe Bedding Material
ClearVu Fencing(R/m) | 2000 |  |  | Access Gate | 20000 | From Trench or Other Excavations | 120
Access Gate | 17500 |  |  |  |  | By Importation From Commerical Sources | 320
Joint Sealing | 830 |  |  | SITE CLEARANCE |  | 110mm dia. uPVC Tee Piece | 380
Blinding (per m2) | 130 |  |  | Clear and grub small trees and bushes | 7230
Landscaping & Grassing (per m2) | 120 |  |  | Clear and grub strip 2 m wide for fence | 10 | JOINTS
Geotextile (per m2) | 23 |  |  |  |  | Joint Filler
|  |  |  | BOX OUT VOIDS |  | 20mm wide between concrete members | 60
Steel covers (1800x1500) | 5000 |  |  | Cylindrical Opening: 0,00-0,01 m³ | 60 | 20mm wide between concrete and brickwork | 170
Steel covers (1800x1350) | 4500 |  |  | Cylindrical Opening: 0,01-0,05 m³ | 380 | Joint Sealer
Steel covers (1800x900) | 3500 |  |  |  |  | 20mm wide between concrete members | 60
Steel covers (900x900) | 2000 |  |  | HIGH TENSILE WELDED MESH |  | 20mm wide between concrete and brickwork | 170
Cast iron Manhole cover (900x900) | 10000 |  |  | Ref. 245 | 60
No fines concrete (per m3) | 200 |  |  | Ref. 193 | 33 | Tee Piece
[6 empty] | 110mm Dia | 300
Joints |  |  |  | JOINTS | 100
Waterstop | 1000 |  |  |  |  | Manhole 1000mm Inside Diameter, 1m ind depth | 1787
Sikadur Joint bandage system | 1375 |  |  | PLASTIC SHEETING | 13 | Concrete Slab | 825
Filler - 150mm conc members | 120 |  |  |  |  | Concrete Manhole Cover | 397
Filler - 200mm conc members | 250 |  |  | SEGMENTED PAVING |  | 590 x 790mm Stormwater Grating & Frame | 5506
Sealant | 450 |  |  | Process Base Material By means of Stabilization | 33 | Kerb Inlet | 16676
Hypalon Bandage | 1200 |  |  | Compaction to 93$% Mod. AASHTO | 34
Hand railing | 1200 |  |  | Portland Cement | 1922 | Manhole Components - 10/11/20
|  |  |  | Kerbing - Fig 3 | 179 | 1000 x 250 Starter Rings | 238
|  |  |  | Kerbing - Edge Beam | 95 | 1000 x 250 Ring with Steps | 251
Ring Beam (m3) | 15000 |  |  | Cutting to Fit Edge Restraints | 11 | Type 2A Covers | 940
Ring Beam (m3) (Excluding reinforcement, conc and FW) | 9500 |  |  |  |  | Type 2A Concrete Frame | 534
|  |  |  | Granular Material | 125
Building Pipes into Concrete (500mm) | 600 |  |  | Selected Fill | 125
Building Pipes into Concrete (600mm) | 900
Box out holes/form voids (1000mm x 1500mm) | 2300
Concrete Strength 15/19 | 120
Benching | 1550
Wood float finish | 35
Steel Float Finish | 45
Rough Finish | 25
Plastic sheeting | 40
Open grid flooring | 4200
Restricted Excavations
0 - 2 | 80
2 - 4 | 100
4 - 6 | 130
Extra over for
Intermediate | 25
Hard Rock | 200
Step irons | 320
Impermeable Waterproofing ductile slurry | 340
Note on O21: Sourced from Rocla
Note on O22: Sourced from Rocla
Note on K41: Calculated From Rocla
Note on K43: Grid Inlet 400x600mm = R2000 from Saint Gobain Africa in 2018 therefor R2000 * 1.06^2 = R2247
Note on O65: From Driefontein WwTW 2018
Note on O66: From Driefontein WwTW 2018

## 2. Site Prep & Fencing
SECTION 2: SITE PREPERATION & FENCING
ITEM NO | PAYMENT CLAUSE | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
SECTION 2: SITE PREPARATION & FENCING
2.1 | SANS 1200C | SITE CLEARANCE
2.1.1 | 8.2.1 | Clear and grub small trees and bushes | ha | 2
2.1.2 | 8.2.1 | Clear and grub strip 2 m wide for fence | m | 455
2.2 | SANS 1200D | EARTHWORKS
| 8.3.1 | Site Preparation
2.2.1 | 8.3.1.2 | Remove topsoil to nominal depth of 150 mm, stockpile and maintain (only where ordered by the Engineer) | m² | 12682
| PSD 8.3.2 | Bulk Excavation
| 8.3.2 (a) | Excavate in all materials and use for embankment or backfill or dispose as ordered within freehaul distance
2.2.2 |  | (1) Excavate to main terrace level of reservoir and ancilliary structures and dispose | m³ | 2560 |  |  | Cut
2.2.3 |  | (2) Excavate to main terrace level of access road and dispose | m³ | 250
2.2.4 |  | Extra over items 2.2.2 to 2.2.3 for additional excavations required by the Engineer after excavation has been completed | m³ | 820
| 8.3.2(b) | Extra over items 2.2.2 to 2.2.3 for excavations in:
2.2.5 |  | (1) Intermediate material | m³ | 1686
2.2.6 |  | (2) Hard rock material | m³ | 843
2.2.7 | 8.3.6 | Overhaul | m³.km | 200
| PSBA | Landscapping and Grassing
Leak Detection
|  | Trimming: |  |  |  |  | 42.3231
2.2.8 | PSBA 8.1 (a) | Machine trimming areas to receive grass | m² | 5290
Preparing areas for grassing (Only where no trimming was done)
2.2.9 | PSBA 8.3 (a) | Scarifying where ordered by the Engineer | m² | 1058
| PSAB 8.3 (b) | Top soiling (100mm thick) with:
2.2.10 |  | Topsoil obtained from stockpile on site | m² | 529
2.2.11 |  | Topsoil obtained by the Contractor (from commercial sources) | m² | 5290
| PSAB 8.3 (d) | Supplying and applying of Chemical Fertiliser @ 50g/m2
2.2.12 |  | 2:3:2 (22) Fertilizer | kg | 264.5
| PSVA 8.4 | Grassing
2.2.13 | PSVA 8.4 (b) | Kikuyu sodding | m² | 1587
2.2.14 | PSVA 8.4 (d) | Hydroseeding mix | m² | 793.5
2.2.15 | PSVA 8.7 | Dealing with weeds | m² | 1322.5
2.2.16 | PSVA 8.8 | Extra over for Landcapping | Prov. Sum | 1 | 50000
SUB-TOTAL CARRIED FORWARD
brought forward
2.3 | PSVB | ACCESS CONTROL AND FENCING |  |  |  |  | 17.46 | 2-3 | #REF!
[7 empty] | 52.29 | 3-4
|  | Supply and erection of new security fencing material |  |  |  |  | Network 2
10.374
2.3.1 | PSVB 8.1 | Supply and Install a new 2.4m Clear Galvanised Steel Mesh Fence | m | 415 |  |  | 106.8113
2.3.2 |  | 600mm Deep by 200mm wide concrete (Class 15/20) strip below fence into ground | m³ | 50
[7 empty] | 85.407 | 2-3 | 85.407
2.3.3 | PSVB 8.2 | Supply and Install a 7m Motorised Galvanised Steel Mesh Sliding Gate to suit 2.4m Galvanised Steel Mesh Fence | No. | 1 |  |  | 226.7265 | 2-4 | 0
TOTAL FOR SECTION 2 (Carried to Summary)
Note on C21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Distance specified somewhere? Reply: Yes, in the doc. anything greater than 1km is overhaul

## 3. Roads & Stormwater
SECTION 3: ROADS & STORMWATER
ITEM NO | PAYMENT CLAUSE | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
SECTION 3: ROADS AND STORMWATER
3.1 | SANS 1200DB | PIPE TRENCHES
| PSD 8.3.2 | Excavate in all materials for trenches, backfill and compact, including disposal of surplus unsuitable material for pipes and cable ducts over 300 mm up to 600 mm diameter for depths.
3.1.1 |  | (a) 0.0 m - 2.0 m | m | 35 | [5 empty] | > Check whether the PS spec is in agreement with the limits specified
> Add PS spec reference
3.1.2 |  | (b) 2.0 m - 4.0 m | m | 5 | [5 empty] | > These quanitites should not include leak detection system - check
3.1.3 |  | Extra over items 3.1.1 to 3.1.2 for additional excavations required by the Employer's Agent after excavation has been completed | m³ | 8
| PSD 8.3.2(b) | Extra over items 3.1.1 to 3.1.2 for
3.1.4 |  | (1) Intermediate excavation | m3 | 5
3.1.5 |  | (2) Hard rock excavation | m3 | 5
3.1.6 | 8.3.2 (c) | Excavate and dispose of unsuitable material from trench bottom (provisional) | m3 | 40
| 8.3.3 | Excavation Ancilliaries
Make up deficiency in backfill material (provisional)
3.1.7 |  | (c) by importation from commercial sources (G7) | m3 | 860
3.1.8 | 8.3.3.4 | Overhaul | m³.km | 200
3.1.9 | 8.3.4 | Particular Items
3.1.10 |  | a) Shore trench opposite structure or service (Provisional) | m | 35
| PSDB 8.3.5 | Existing Services that Intersect or Adjoin a Pipe Trench
3.1.11 |  | (a) Services that intersect with the trench | No. | 10
3.1.12 |  | (b) Services that adjoin a trench | m | 50
| 8.3.6 | Finishing
3.1.13 | 8.3.6.1 | Reinstate road sidewalk complete with all courses at pipe crossings as per existing layerworks and surface treatment | m² | 50
3.2 | SANS 1200DM | ACCESS ROAD
| 8.3.3 | Treatment of road-bed
| 8.3.3.3 (a) | Road Bed Preparatioin and Compaction of Materal to:
3.2.1 |  | Rip and recompact in-situ material to 150mm depth, moisten and compact to minimum of 93% Mod. AASHTO density. | m3 | 45
3.2.2 |  | Tie into existing road | Sum | 1
3.3 | SANS 1200G | CONCRETE ROAD
| 8.2 | Formwork
3.3.1 | 8.2.1 | Rough Formwork along sides of concrete road slabs | m | 90
| 8.3 | Reinforcement |  |  |  |  | #REF! | #REF!
3.3.2 | 8.3.1 | High tensile steel bars | t | 0.5 |  |  |  | 0.6 | 0.15 | 0.3 | 0.45
3.3.3 | 8.3.1 | Mild steel bars | t | 0.225
| 8.3.2 | High Tensile Welded Mesh
3.3.4 |  | Ref. 888 for road slabs | m2 | 500
SUB-TOTAL CARRIED FORWARD
brought forward
| 8.4 | Concrete
| 8.4.3 | Strength Concrete of Class 20/19 utilised for:
3.3.5 |  | (a) Road Surface Slab | m³ | 100
| 8.4.4 | Unformed Surface Finishes
3.3.6 |  | (a) Wood-Floated Finish for road slab | m2 | 500
3.4 | PSG 8.5 | JOINTS
| PSG 8.5.2 | Filled Joints
Joint filler consisting of closed cell expanded polyethylene with density not less than 120kg/m3 including bullnose finish to both sides of joint and tear off strip
3.4.1 |  | 20 mm wide between 200mm concrete members | m | 240
| PSG 8.5.3 | Sealed Joints
Joint sealer (20 x 15 mm) consisting of a two component polyether based polyurethane sealing compound on visible face of joint including primer and bond breaker
3.4.2 | (a) | 20 mm x 15 mm joints between concrete members | m | 240 | [5 empty] | >Ask DP to change the silicone to Polyeurethane material
3.4.3 |  | Saw-cut Joints | m | 240 | [5 empty] | > Include Saw-cut Joints as per the drawings
3.5 | SANS 1200LB | PIPE BEDDING
| 8.2.2 | Supply only of Bedding by Importation
| 8.2.2.3 | From commercial sources
3.5.1 | (a) | Selected granular material (G7) compacted to 95% MOD AASHTO | m3 | 9.35
3.5.2 | (b) | Selected fill blanket | m3 | 14.4375
3.5.3 | 8.2.4 | Encasing of 450 mm pipe in 15 MPa concrete | m3 | 33 | [5 empty] | > Check this with the PS specs and add reference to it
3.6 | SANS 1200LE | STORMWATER DRAINAGE
| 8.2.1 | Supply, handle, lay, bed Class B concrete pipes with interlocking joints
3.6.1 |  | 450 mm diameter Class 100D | m | 35
3.6.2 |  | Ancilliary Stormwater Infrastructure | Prov. Sum | 1 | 350000
3.7 | SANS 1200ME | SUBBASE
| 8.3.3 | Construct the subbase course/ shoulder with material from commercial sources or designated borrow pits.
3.7.1 |  | G7 material compacted in 150mm layer to 93% of modified AASHTO maximum density. | m3 | 45
3.7.2 |  | Construct 150mm layer of G5 base compacted to 93% of MOD AASHTO from commercial sources | m3 | 45
3.8 | SANS 1200MF | STABILISATION
3.8.1 | 8.3.5 | Process base material by Stabilisation | m3 | 45
| 8.3.8 | Stabilising Agent:
[7 empty] | 1-2 | #REF!
3.8.2 | 8.3.8 (b) | Portland Cement | t | 9.3447 |  |  | 2-3 | #REF!
3.9 | SANS 1200MK | KERBING & CHANNELLING
| 8.2.1 | Concrete kerbing (Class 20/20 Concrete)
3.9.1 |  | Edge beam (150mm x 150mm) | m³ | 1.125
SUB-TOTAL CARRIED FORWARD
brought forward
3.9.2 |  | 300 x 150mm Barrier kerb (Straight) Fig 3 | m | 125
3.9.3 |  | Allowance for 80mm thick interlocking paving blocks | Prov. Sum | 1 | 950000 | 950000
3.1 | SANS 1200MM | ANCILLIARY ROADWORKS
3.10.1 |  | Allowance for signage, barriers and markings | Prov. Sum | 1 | 100000 | 100000
3.10.2 |  | Tie into road stormwater network | Prov. Sum | 1 | 250000 | 250000
PROVISION FOR PAVING
3.11 | SANS 1200ME | SUBBASE
3.11.1 |  | Rip and recompact in-situ material to 150mm depth, moisten and compact to minimum of 93% Mod. AASHTO density. | m3 | 800
3.11.2 | 8.3.3 | Construct the subbase course/ shoulder with material from commercial sources or designated borrow pits. | m3 | 800
3.11.3 |  | Construct 150mm layer of G5 base compacted to 93% of MOD AASHTO from commercial sources | m3 | 800
3.11.4 |  | 150 mm C4 compacted to 95% MOD. AASHTO. | m3 | 800
3.11.5 | 8.3.8 (b) | Stabilizing agent: Portland cement (3%) | t | 30
TOTAL FOR SECTION 3 (Carried to Summary)
Note on C29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Specify whether G5, G6, G7 or G8 - might get G10 otherwise
Note on C115: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: specify grade eg G6... Reply: NG to assist
Note on C147: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 20/19?

## 4.Reservoir
SECTION 4: RESERVOIR
ITEM NO | PAYMENT CLAUSE | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
SECTION 4: RESERVOIR
4.1 | SANS 1200D | EARTHWORKS
| 8.3.3 | RESTRICTED EXCAVATION
| PSD 8.3.3(a) | Excavate for restricted foundations, footings and pipe trenches in all materials and use as described for items 4.1.1 to 4.1.3
4.1.1 |  | 0 to 2m deep | m³ | 900
4.1.2 |  | 2m to 4m deep | m³ | 300
| PSD 8.3.3 (b) | Extra over items 4.1.1 to 4.1.2 for
4.1.3 | 1) | Intermediate excavation | m³ | 450
4.1.4 | 2) | Hard rock excavation | m³ | 450
4.1.5 |  | Extra over items 4.1.1 to 4.1.4 for additional excavations required by the Engineer after excavation has been completed | m³ | 180
4.1.6 | 8.3.6 | Overhaul | m³.km | 11250
4.2 | SANS 1200L | PIPEWORK
| PSL 8.2.5 | PIPE SPECIALS
4.2.1 |  | Supply, testing and installation of pipework, fittings and specials brought forward from the Pipe Schedule (building in of pipes measured elsewhere) | Sum | 1
4.3 | PSLD | BUILDING PIPES INTO CONCRETE WORK
| 8.3 (a) | Pipes supplied and installed by the Contractor (Irrespective of type)
4.3.1 |  | 150 mm diameter | No. | 1
4.3.2 |  | 500 mm diameter | No. | 1
4.3.3 |  | 600 mm diameter | No. | 1
4.4 | SANS 1200G | CONCRETE (STRUCTURAL)
| 8.2 | Formwork
| 8.2.2 | Smooth Formwork
Plane Vertical
4.4.1 |  | Drainage trench walls | m² | 55
4.4.2 |  | Edges of butresses | m² | 140
Curved Cylindrical
4.4.3 |  | Vertical sides of reservoir wall footing (outer radius 30175 mm) | m² | 90
4.4.4 |  | Vertical sides of reservoir wall footing (inner radius 28125 mm) | m² | 80
4.4.5 |  | Wall of reservoir (outer radius 29450 mm) | m² | 1575
4.4.6 |  | Wall of reservoir (inner radius 29000 mm) | m² | 1550
4.4.7 |  | Ring beam (outer radius 29800 mm) | m² | 255
4.4.8 |  | Ring beam (inner radius 29000 mm) | m² | 150
4.4.9 |  | Roof Vent | m² | 12.5
| 8.2.5 | Narrow width (up to 300mm wide)
4.4.10 |  | Sides of drainage trench floor (250mm high) | m | 41
SUB-TOTAL CARRIED FORWARD
brought forward
4.4.11 |  | Edge of apron around reservoir | m | 195
Curved Spherical
4.4.12 |  | Internal soffit of reservoir roof | m² | 3060
| 8.2.6 | Box Out Holes/Form Voids
4.4.13 | 8.2.6(d) | Rectangular openings for access hatch A (1000 x 1500 mm) as shown in drawing: 13214-73-04-001 | No. | 2
| PSG 8.2.7 | Chamfers larger than 20mm x 20mm
4.4.14 |  | 25 mm along ringbeam | m | 370
4.4.15 |  | 25mm roof ventilator | m | 7.6
4.4.16 |  | 60x60 Plastic fillet along prestressed reservoir wall as per drawing 13214-73-04-001 | m | 185
| 8.3 | Reinforcement
4.4.17 | 8.3.1 | High tensile steel bars | t | 249
4.4.18 | 8.3.1 | Mild steel bars | t | 22
| 8.4 | Concrete
| PSG 8.4.3 | Strength of Concrete: 15/19
4.4.19 | 8.4.2 | Blinding layer 75mm thick in reservoir floor and footing (horizontal) | m² | 3010
4.4.20 |  | Blinding layer 50mm thick underneath drainage trench as per drawing 13214-73-04-001 | m² | 30
STRENGTH CONCRETE NF 20
4.4.21 |  | No fines concrete layer 100mm thick (horizontal) in reservoir floor | m² | 2645
4.4.22 |  | 300 x 300 mm No fines concrete around 110 diameter slotted PVC pipe as per drawing 13214-73-04-002 | m³ | 40
4.4.23 |  | No fines concrete around 75 diameter perforated PVC pipe within the leak detection system as per drawing 13214-73-04-002 | m³ | 30
4.4.24 |  | Mass concrete as ordered by the engineer | m³ | 100
| PSG 8.4.3 | Strength of Concrete: 25/19
4.4.25 |  | Apron Slab | m³ | 140
| PSG 8.4.3 | Strength of Concrete: 35/19
4.4.26 |  | Wall Footings | m³ | 145
4.4.27 |  | Floors | m³ | 530
4.4.28 |  | Walls (including 350 x 2000 Buttresses) | m³ | 760
4.4.29 |  | Ring beam | m³ | 255
4.4.30 |  | Roof (including base of ventilation structure) | m³ | 845
4.4.31 |  | Drainage trench floor | m³ | 15
4.4.32 |  | Drainage trench walls | m³ | 10
| 8.4.4 | Unformed Surface Finishes
| 8.4.4 (a) | Wood Floated Finish
4.4.33 |  | Drainage trench (floor and top of walls) | m² | 45
4.4.34 |  | Domed roof | m² | 3060
SUB-TOTAL CARRIED FORWARD
brought forward
| 8.4.4 (b) | Steel Floated Finish
4.4.35 |  | Floor inside reservoir | m² | 2670
| PSG 8.9 | Sealing of openings in top surface of NF-concrete layer with plaster
4.4.36 |  | horizontal | m² | 2670
4.5 | PSG 8.5 | JOINTS
Filled Joints (Including Formwork)
Joint Filler Consisting of Closed Cell Expanded Polyethylene with Density not Less than 100 kg/m3 Including Bullnose Finish to Both Sides of Joint.
4.5.1 |  | 20 mm wide between 100 mm concrete members | m | 190
4.5.2 |  | 20 mm wide between 150 mm concrete members | m | 190
4.5.3 |  | 20 mm wide between 200 mm concrete members | m | 645
| PSG 8.5.3 | Sealed Joints
Joint Sealer (20 X 15 mm) Consisting of a two Component Polyether Based Polyurethane Sealing Compound on Visible Face of Joint Including Primer and Backing Cord or Bond Breaker
4.5.4 |  | 20 mm joints between concrete wall and floor interface as per drawings 13214-73-04-001 | m | 735
4.5.5 |  | 20 mm wide sealed expansion joint along perimeter of drainage trench as per drawing 13214-73-04-001 | m | 55
4.5.6 |  | 20 mm expansion joint along reservoir floor | m | 450
| PSG 8.5.4 | Waterstops
4.5.7 | (a) | 200 mm wide Rearguard with centerbulb PVC waterstop at floor joints | m | 450
4.5.8 | (b) | 250 mm Rearguard with centerbulb PVC waterstop at wall and floor joint (29m radius) | m | 183
4.5.9 | (c) | Extra-over items (a) and (b) above for factory moulded intersection pieces | No. | 30
| PSG 8.5.5 | Bandaged Joints
4.5.10 | (a) | 200mm wide X 2mm thick epoxy-fixed bandage along floor expansion joints | m | 450
4.5.11 | (b) | 250mm wide x 2mm thick flexible epoxy-fixed bandage along horisontal wall construction joints | m | 1095
4.5.12 | (c) | 300mm wide X 2mm thick flexible epoxy-fixed bandage along wall and floor expansion joints (90 degree angle) incl. 60x60 corner fillet | m | 183
Sundry Items
4.6 |  | PLASTIC SHEETING
4.6.1 | PSLE 8.2.18 | 250 micron PVC sheeting underneath floor slab | m² | 2610
4.6.2 |  | 200 micron PVC sheeting adjacent to scour pipe as per drawing 13214-73-04-003: Scour Pipe Detail | m² | 1872
4.7 |  | BEARING STRIPS
4.7.1 |  | Supply and install 200 kN/m strip bearing at reservoir footing as per drawing 13214-73-04-001: Prestressed Wall/Footing Detail | m | 185
4.7.2 |  | Supply and install 95 kN/m strip bearing on top of reservoir wall as per drawing 13214-73-04-001: Ringbeam Detail | m | 185
SUB-TOTAL CARRIED FORWARD
brought forward
4.8 | PSG 8.13 | WATERPROOFING
4.8.1 |  | Impermeable ductile slurry coating on all internal tank wall and floor surfaces. Including the top external surface of the tank roof. | m² | 11000
4.9 | PSG 8.10 | TESTING STRUCTURE FOR WATERTIGHTNESS
4.9.1 |  | Reservoir | No. | 1
4.1 | SANS 1200HA | STRUCTURAL STEELWORK
Ladder
4.10.1 |  | Heavy Duty Hot Dipped Galvanised SABS 763 - as per drawing 13214-73-04-002: Typical Cat Ladder Detail | No. | 2
4.10.2 |  | Stainless Steel Grade 304 Access ladder including cage as per drawing 13214-73-04-002: Typical Cat Ladder Detail | No. | 1
4.10.3 |  | Stainless Steel Grade 304 grating to fit in a stainless steel frame to be placed over outlet and scour pipes as per drawing 13214-73-04-003 | No. | 2
4.10.4 |  | Stainless Steel Grade 304 energy dissipating plate 4.5mm thick bolted to Reservoir wall with a neoprene rubber inbetween installed below inlet pipe as per drawing 13214-73-04-003 | No. | 1
GRP Products
4.10.5 |  | GRP handrail assembly complete | m | 200
Access Hatch
4.10.6 |  | Lockable access hatch (1000mm x 1500mm) as per drawing 13214-73-04-002: Plan on Access Hatch | No. | 2
4.11 | SANS 1200L | MEDIUM PRESSURE PIPELINES
| 8.2.2 | Specials and Fittings
Extra over for the supply & installation of fittings and specials as shown in drawing 13214-73-04-002: Typical Cross & T Connection
4.11.1 |  | (a) 110 diameter PVC cross | No. | 10
4.11.2 |  | (b) 110 diameter PVC tee | No. | 8
Mild Steel Pipes
4.11.3 |  | 50 mm Galvanised MS outlet pipes | No. | 31
4.12 | PSG 8.11 | RESERVOIR STERILIZATION
4.12.1 |  | Sterilization of the reservoir | Sum | 1
4.13 | PSU 8.14 | ROOF VENTILATOR
4.13.1 |  | Supply and install Roof ventilator as per the detail on drawing 13214-73-04-001: Roof Ventilator Detail | Sum | 1
TOTAL FOR SECTION 4 (Carried to Summary)

## 6.Interconnecting Pipework (2) (hidden)
PROJECT NUMBER: EI1306
CARLSWALD 20ML RESERVOIR
SCHEDULE OF QUANTITIES
SECTION 6: INTERCONNECTING PIPEWORK
ITEM | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT | Notes
NO | CLAUSE | [5 empty] | Numbers to be updated
Formatting to be fixed
| SANS 1200DB | PIPE TRENCHES |  |  |  |  | Levels to be confirmed and updated
Piping config to be confirmed
|  | EXCAVATION |  |  |  |  | Valves & Pipe Specials to be confirmed
Revise concrete grades as per EFM Spec
| 8.3.2 | EXCAVATE IN ALL MATERIALS FOR TRENCHES, BACKFILL AND COMPACT, INCLUDING DISPOSAL OF SURPLUS UNSUITABLE MATERNAL FOR PIPES
UP TO 300 mm DIAMETER FOR DEPTHS OVER AND UP TO
|  | 0.0 m - 1.0 m | m | 47.5 | 60 | 2850
|  | 1.0 m - 2.0 m | m | 84.5 | 132 | 11154
|  | 2.0 m - 3.0 m | m | 178 | 215 | 38270
OVER 300 mm UP TO 600 mm DIAMETER FOR DEPTHS
|  | 0.0 m - 1.0 m | m | 462 | 86 | 39732
|  | 1.0 m - 2.0 m | m | 462 | 188 | 86856
|  | 2.0 m - 3.0 m | m | 202 | 308 | 62216
|  | 3.0 m - 4.0 m | m | 20 | 442 | 8840
| 8.3.2 (b) | EXTRA OVER ITEMS 15.1.1 TO 15.1.9 FOR EXCAVATIONS
| 8.3.2 (I) | Intermediate material | m3 | 366 | 375 | 137250
| 8.3.2 (ii) | Hard rock material | m3 | 237.5 | 1182 | 280725
| SANS 1200LB | BEDDING
| 8.2.2.1 | PROVISION OF BEDDING MATERIAL FROM TRENCH OR OTHER EXCAVATIONS WITHIN FREEHAUL DISTANCE
| (a) | Selected granular material | m3 | 90 | 125 | 11250
| (b) | Selected fill blanket | m3 | 115 | 125 | 14375
| 8.2.2.3 | PROVISION OF BEDDING MATERIAL BY IMPORTATION FROM COMMERCIAL SOURCES
| (a) | Selected granular material | m3 | 90 | 325 | 29250
|  | SUB-TOTAL CARRIED FORWARD |  |  |  | 722768
|  | brought forward |  |  |  | 722768
| (b) | Selected fill blanket | m3 | 115 | 325 | 37375
CONCRETE AT PIPES
| 8.2.4 | Encasing of 110mm dia underfloor drainage pipes in concrete | m³ | 60 | 2800 | 168000
| 8.2.4 | Encasing of 150mm dia drainage & scour pipes in concrete | m³ | 8 | 2800 | 22400
| 8.2.4 | Encasing of 350mm dia overflow pipe in concrete | m³ | 4 | 2800 | 11200
| 8.2.4 | Encasing of 500mm dia inlet pipe in concrete | m³ | 10 | 2800 | 28000
| 8.2.4 | Encasing of 600mm dia outlet pipe in concrete | m³ | 15 | 2800 | 42000
PLASTIC SHEETING
|  | 250 micron pvc sheeting underneath floor slab | m² | 795 | 40 | 31800 | check this with NG or bidim
| SANS 1200L | INLET
PIPEWORK
| 8.2.1 | SUPPLY, LAY, JOIN AND TEST PIPEWORK
| PSL | PIPE SPECIALS
8.2.5
|  | Testing of pipes, fittings and specials brought forward from the pipe schedule for Interconnecting Pipe Work (building in of pipes measured elsewhere) | Sum | 1 | 100000 | 100000 | The correct wording for this item is …... And it is for the total amount in the pipe schedule for this section | Supplying, testing and installation of pipes, fittings and specials brought forward from the Pipe Schedule
|  | 500mm dia Stainless steel puddle pipe 750mm long. Both ends flanged, with puddle flange 375mm from one end | No | 2 | 50000 | 100000
|  | 300mm dia stainless steel flanged pipe 3500mm long | No | 2 | 25000 | 50000
|  | 300mm dia stainless steel flanged pipe 1750mm long | No | 4 | 17500 | 70000
Y-PIECE
|  | 500mm dia stainless steel flanged Y-Piece | No | 2 | 85000 | 170000
45' BEND
|  | 500mm dia 45' Short radius bend | No | 4 | 48000 | 192000
|  | SUB-TOTAL CARRIED FORWARD |  |  |  | 1745543
|  | brought forward |  |  |  | 1745543
ECCENTRIC REDUCER
|  | 500mm x 300mm dia stainless steel flanged eccentric reducer, 290mm long | No | 4 | 60000 | 240000
INLINE STRAINER
|  | 300mm stainless steel inline strainer 760mm long | No | 2 | 50000 | 100000
GATE VALVE
|  | 300mm dia geared wedge gate valve, double flanged | No | 4 | 100000 | 400000
CONTROL VALVE
|  | 300mm dia control valve | No | 2 | 150000 | 300000
FLANGE ADAPTOR
|  | 300mm dia flange adaptor | No | 4 | 10000 | 40000
Extra Over
|  | Valves | Sum | 1 | 300000 | 300000
| SANS 1200L | OUTLET
PIPEWORK
| 8.2.1 | SUPPLY, LAY, JOIN AND TEST PIPEWORK
| PSL | PIPE SPECIALS
8.2.5
|  | Testing of pipes, fittings and specials brought forward from the pipe schedule for Interconnecting Pipe Work (building in of pipes measured elsewhere) | Sum | 1 | 100000 | 100000
|  | 600mm dia stainless steel puddle pipe 750mm long. Both ends flanged, with puddle flange 375mm from one end | No | 2 | 90000 | 180000
|  | 600mm dia stainless steel flanged pipe 1000mm long | No | 1 | 80000 | 80000
|  | 600mm dia stainless steel flanged pipe 600mm long | No | 1 | 50000 | 50000
Y-PIECE
|  | 600mm dia stainless steel flanged Y-Piece | No | 2 | 125000 | 250000
|  | SUB-TOTAL CARRIED FORWARD |  |  |  | 3785543
|  | brought forward |  |  |  | 3785543
45' BEND
|  | 600mm dia 45' Short radius bend | No | 4 | 75000 | 300000
EQUAL TEE
|  | 600mm stainless steel flanged unequal tee, 3500mm long | No | 2 | 110000 | 220000 | Are there 2?
AIR VALVE
|  | 600mm Ventomat double orrifice, anti-shock, geared air valve screw ended | No | 2 | 100000 | 200000
GATE VALVE
|  | 600mm dia acctuated wedge gate valve, double flanged | No | 2 | 350000 | 700000
BALL VALVE
|  | 50mm dia ball valve | No | 2 | 3000 | 6000
|  | 100mm dia ball valve | No | 2 | 6000 | 12000
FLANGE ADAPTOR
|  | 600mm dia flange adaptor | No | 2 | 25000 | 50000
NON RETURN VALVE
|  | 600mm Non-Reurn valve | No | 2 | 455000 | 910000 | Why 2?
Extra Over
|  | Valves | Sum | 1 | 300000 | 300000
| SANS 1200L | SAMPLE INLET, OUTLET & MAINTENANCE PIPES
PIPEWORK
| 8.2.1 | SUPPLY, LAY, JOIN AND TEST PIPEWORK
|  | 50mm dia stainless steel pipe 6000mm long | No | 7 | 9000 | 63000
90' BEND
|  | 50mm dia 90' Short radius bend | No | 18 | 500 | 9000
BALL VALVE
|  | SUB-TOTAL CARRIED FORWARD |  |  |  | 6555543
|  | brought forward |  |  |  | 6555543
|  | 50mm dia ball valve | No | 2 | 3000 | 6000
Extra Over
|  | Pipe Specials | Sum | 1 | 25000 | 25000
| SANS 1200L | INLET FLOW METER CHAMBER
PIPEWORK
| 8.2.1 | SUPPLY, LAY, JOIN AND TEST PIPEWORK
| PSL | PIPE SPECIALS
8.2.5
|  | Testing of pipes, fittings and specials brought forward from the pipe schedule for Interconnecting Pipe Work (building in of pipes measured elsewhere) | Sum | 1 | 50000 | 50000
|  | 500mm dia stainless steel puddle pipe 900mm long. Both ends flanged, with puddle flange 350mm from one end | No | 2 | 55000 | 110000
|  | 500mm dia stainless steel flanged pipe 2100mm long | No | 1 | 58000 | 58000
FLANGE ADAPTOR
|  | 500mm dia flange adaptor | No | 1 | 20000 | 20000
Extra Over
|  | Pipe Specials | Sum | 1 | 50000 | 50000
| SANS 1200L | OUTLET FLOW METER CHAMBER
PIPEWORK
| 8.2.1 | SUPPLY, LAY, JOIN AND TEST PIPEWORK
| PSL | PIPE SPECIALS
8.2.5
|  | Testing of pipes, fittings and specials brought forward from the pipe schedule for Interconnecting Pipe Work (building in of pipes measured elsewhere) | Sum | 1 | 50000 | 50000
|  | 600mm dia stainless steel puddle pipe 900mm long. Both ends flanged, with puddle flange 350mm from one end | No | 1 | 85000 | 85000
|  | 600mm dia stainless steel flanged pipe 2100mm long | No | 1 | 85000 | 85000
|  | SUB-TOTAL CARRIED FORWARD |  |  |  | 7094543
|  | brought forward |  |  |  | 7094543
FLANGE ADAPTOR
|  | 600mm dia flange adaptor | No | 1 | 25000 | 25000
Extra Over
|  | Pipe Specials | Sum | 1 | 50000 | 50000
| SANS 1200L | SCOUR CHAMBER
PIPEWORK
| 8.2.1 | SUPPLY, LAY, JOIN, BED CLASS B AND TEST epoxy coated mild steel PIPEWORK
| PSL | PIPE SPECIALS
8.2.5
|  | Testing of pipes, fittings and specials brought forward from the pipe schedule for Interconnecting Pipe Work (building in of pipes measured elsewhere) | Sum | 1 | 100000 | 100000
|  | 150mm dia stainless steel puddle pipe 1050mm long. Both ends flanged, with puddle flange 400mm from one end | No | 1 | 10500 | 10500
|  | 150mm dia stainless steel puddle pipe 1050mm long. Both ends flanged, with puddle flange 400mm from one end including tap off | No | 1 | 15000 | 15000
|  | 350mm dia stainless steel puddle pipe 1050mm long. One end flanged, with puddle flange 400mm from one end | No | 1 | 30000 | 30000
|  | 150mm dia stainless steel puddle pipe 955mm long. One end flanged, with puddle flange 705mm from one end | No | 1 | 12500 | 12500
GATE VALVE
|  | 150mm dia wedge gate valve, double flanged | No | 2 | 50000 | 100000
BALL VALVE
|  | 50mm dia ball valve | No | 1 | 3000 | 3000
Extra Over
|  | Pipe Specials | Sum | 1 | 100000 | 100000
| SANS 1200L | OUTLET PIPEWORK
|  | SUB-TOTAL CARRIED FORWARD |  |  |  | 7540543
|  | brought forward |  |  |  | 7540543
PIPEWORK
| 8.2.1 | SUPPLY, LAY, JOIN, BED CLASS B AND TEST epoxy coated mild steel PIPEWORK
| PSL | PIPE SPECIALS
8.2.5
|  | Testing of pipes, fittings and specials brought forward from the pipe schedule for Interconnecting Pipe Work (building in of pipes measured elsewhere) | Sum | 1 | 200000 | 200000
|  | 600mm dia epoxy coated mild steel flanged pipe 6000mm long | No | 15 | 70000 | 1050000
|  | 600mm dia epoxy coated mild steel flanged pipe 4441mm long | No | 1 | 60000 | 60000
|  | 600mm dia epoxy coated mild steel flanged pipe 3191mm long | No | 1 | 50000 | 50000
|  | 600mm dia epoxy coated mild steel single flanged pipe 4441mm long | No | 1 | 60000 | 60000
|  | 600mm dia stainless steel flanged pipe 625mm long | No | 1 | 70000 | 70000
|  | 600mm dia stainless steel flanged pipe 2475mm long | No | 1 | 95000 | 95000
|  | 600mm dia stainless steel flanged pipe 1885mm long | No | 1 | 85000 | 85000
FLANGE ADAPTOR
|  | 600mm dia epoxy coated mild steel flange adaptor | No | 1 | 25000 | 25000
90' BEND
|  | 600mm dia epoxy coated mild steel flanged 90' medium radius bend | No | 1 | 45000 | 45000
|  | 600mm dia stainless steel flanged 90' medium radius bend, 2440mm centre to flange | No | 1 | 130000 | 130000
EQUAL TEE
|  | 600mm epoxy coated mild steel flanged equal tee 610mm centre to flange | No | 1 | 35000 | 35000
BELLMOUTH
|  | 600mm stainless steel flanged bellmouth 750mm long with 1800mm dia bellmouth | No | 1 | 100000 | 100000
|  | SUB-TOTAL CARRIED FORWARD |  |  |  | 9545543
|  | brought forward |  |  |  | 9545543
|  | Pipe Jacking | Sum | 1 | 400000 | 400000
|  | Tie into exisiting line | Sum | 1 | 10000 | 10000
Extra Over
|  | Pipe Specials | Sum | 1 | 250000 | 250000
| SANS 1200L | INLET PIPEWORK
PIPEWORK
| 8.2.1 | SUPPLY, LAY, JOIN, BED CLASS B AND TEST epoxy coated mild steel PIPEWORK
| PSL | PIPE SPECIALS
8.2.5
|  | Testing of pipes, fittings and specials brought forward from the pipe schedule for Interconnecting Pipe Work (building in of pipes measured elsewhere) | Sum | 1 | 200000 | 200000
|  | 500mm dia epoxy coated mild steel flanged pipe 6000mm long | No | 13 | 60000 | 780000
|  | 500mm dia epoxy coated mild steel flanged pipe 1093mm long | No | 1 | 35000 | 35000
|  | 500mm dia stainless steel flanged pipe 3194mm long | No | 1 | 50000 | 50000
|  | 500mm dia epoxy coated mild steel flanged pipe 2190mm long | No | 2 | 40000 | 80000
|  | 500mm dia epoxy coated mild steel flanged pipe 5960mm long | No | 2 | 60000 | 120000
EQUAL TEE
|  | 500mm epoxy coated mild steel flanged equal tee 460mm centre to flange | No | 1 | 75000 | 75000
90' BEND
|  | 500mm dia stainless steel flanged 90' medium radius bend, 1020mm centre to flange | No | 3 | 60000 | 180000
|  | 500mm dia stainless steel flanged 90' short radius bend | No | 3 | 55000 | 165000
FLANGE ADAPTOR
|  | SUB-TOTAL CARRIED FORWARD |  |  |  | 11890543
|  | brought forward |  |  |  | 11890543
|  | 500mm dia epoxy coated mild steel flange adaptor | No | 1 | 20000 | 20000
|  | Pipe Jacking | Sum | 1 | 100000 | 100000
|  | Tie into exisiting line | Sum | 1 | 10000 | 10000
Extra Over
|  | Pipe Specials | Sum | 1 | 250000 | 250000
| SANS 1200L | OVERFLOW PIPEWORK
PIPEWORK
| 8.2.1 | SUPPLY, LAY, JOIN, BED CLASS B AND TEST epoxy coated mild steel PIPEWORK
| PSL | PIPE SPECIALS
8.2.5
|  | Testing of pipes, fittings and specials brought forward from the pipe schedule for Interconnecting Pipe Work (building in of pipes measured elsewhere) | Sum | 1 | 100000 | 100000
|  | 350mm dia epoxy coated mild steel flanged pipe 4200mm long | No | 1 | 18000 | 18000
|  | 350mm dia stainless steel flanged pipe 6000mm long | No | 1 | 42000 | 42000
90' BEND
|  | 350mm dia stainless steel flanged 90' short radius bend, 360mm centre to flange | No | 1 | 30000 | 30000
BELLMOUTH
|  | 350mm stainless steel flanged bellmouth 3465mm long with 535mm dia bellmouth | No | 1 | 35000 | 35000
Extra Over
|  | Pipe Specials | Sum | 1 | 250000 | 250000
| SANS 1200L | DRAINAGE PIPEWORK
PIPEWORK
|  | SUB-TOTAL CARRIED FORWARD |  |  |  | 12745543
|  | brought forward |  |  |  | 12745543
| 8.2.1 | SUPPLY, LAY, JOIN, BED CLASS B AND TEST epoxy coated mild steel PIPEWORK
| PSL | PIPE SPECIALS
8.2.5
|  | Testing of pipes, fittings and specials brought forward from the pipe schedule for Interconnecting Pipe Work (building in of pipes measured elsewhere) | Sum | 1 | 100000 | 100000
|  | 150mm dia epoxy coated mild steel flanged pipe 6000mm long | No | 3 | 60000 | 180000
|  | 150mm dia epoxy coated mild steel flanged pipe 2170mm long | No | 1 | 3000 | 3000
|  | 150mm dia epoxy coated mild steel puddle pipe 1250mm long. One end flanged, with puddle flange 125mm from one end | No | 1 | 3000 | 3000
45' BEND
|  | 150mm dia epoxy coated mild steel flanged 45' short radius bend, 230mm centre to flange | No | 1 | 3000 | 3000
90' BEND
|  | 150mm dia epoxy coated mild steel flanged 90' medium radius bend, 230mm centre to flange | No | 1 | 4000 | 4000
Extra Over
|  | Pipe Specials | Sum | 1 | 100000 | 100000
| SANS 1200L | SCOUR PIPEWORK
PIPEWORK
| 8.2.1 | SUPPLY, LAY, JOIN, BED CLASS B AND TEST epoxy coated mild steel PIPEWORK
| PSL | PIPE SPECIALS
8.2.5
|  | Testing of pipes, fittings and specials brought forward from the pipe schedule for Interconnecting Pipe Work (building in of pipes measured elsewhere) | Sum | 1 | 100000 | 100000
|  | 150mm dia epoxy coated mild steel flanged pipe 3385mm long | No | 1 | 5000 | 5000
|  | SUB-TOTAL CARRIED FORWARD |  |  |  | 13243543
|  | brought forward |  |  |  | 13243543
90' BEND
|  | 150mm dia Stainless steel flanged 90' short radius bend, 230mm centre to flange | No | 1 | 8000 | 8000
BELLMOUTH
|  | 150mm stainless steel flanged bellmouth 1820mm long with 230mm dia bellmouth | No | 1 | 8000 | 8000
Extra Over
|  | Pipe Specials | Sum | 1 | 100000 | 100000
| SANS 1200L | UNDERFLOOR DRAINAGE
PIPEWORK
|  | Testing of pipes, fittings and specials brought forward from the pipe schedule for Interconnecting Pipe Work (building in of pipes measured elsewhere) | Sum | 1 | 100000 | 100000
| 8.2.1 | SUPPLY, LAY, JOIN, ENCASE AND TEST SLOTED uPVC CLASS 6 (Z-LOCK JOINTS)
|  | 50 mm diameter | m | 75 | 150 | 11250
| 8.2.1 | SUPPLY, LAY, JOIN, ENCASE AND TEST uPVC CLASS 6 (Z-LOCK JOINTS)
|  | 75 mm diameter | m | 310 | 180 | 55800
| 8.2.1 | SUPPLY, LAY, JOIN, ENCASE AND TEST uPVC CLASS 6 (Z-LOCK JOINTS)
|  | 110 mm diameter | m | 340 | 210 | 71400
TOTAL FOR SECTION 6 (Carried to Summary) | [5 empty] | 13597993
Note on G191: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Removed - this is one of the hiding of money items lol.

## 5.Chambers & Boxes
SECTION 5: CHAMBERS & BOXES
ITEM NO | PAYMENT CLAUSE | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
SECTION 5: CHAMBERS AND BOXES
5.1 |  | SCOUR CHAMBER
5.1.1 | SANS 1200D | EARTHWORKS
| PSD 8.3.3 | Restricted Excavation
| PSD 8.3.3(a) | Excavate for Restricted Foundations, Footings and Pipe Trenches in all materials and use as described for Items
5.1.1.1 |  | 0 to 2m deep | m³ | 110
5.1.1.2 |  | 2m to 4m deep | m³ | 95
| PSD 8.3.3 (b) | Extra over items 5.1.1 to 5.1.2 for
5.1.1.3 | 1) | Intermediate excavation | m³ | 98
5.1.1.4 | 2) | Hard rock material | m³ | 42
5.1.1.5 |  | Extra over items 5.1.1.3 to 5.1.1.4 for additional excavations required by the Engineer after excavation has been completed | m³ | 50
5.1.1.6 | 8.3.6 | Overhaul | m³.km | 50
5.1.2 | SANS 1200G | CONCRETE (STRUCTURAL)
| 8.2 | Formwork
| 8.2.2 | Smooth Formwork
Plane Vertical
5.1.2.1 |  | Scour chamber walls (internal and external) | m² | 160
5.1.2.2 |  | Scour chamber floors | m² | 25
5.1.2.3 |  | Sides of valve supports | m² | 1.5
| PSG 8.2.7 | Chamfers larger than 20mm x 20mm
5.1.2.4 |  | 25 x 25 mm along scourbox cover | m | 15
5.1.2.5 |  | 25 x 25 mm along walls of scourbox | m | 20
| PSG 8.3 | Reinforcement
5.1.2.6 | 8.3.1 | High tensile steel bars | t | 5
5.1.2.7 | 8.3.1 | Mild steel bars | t | 2
5.1.2.8 | 8.4 | Strength of Concrete: 15/19
5.1.2.9 |  | Benching to floors of boxes | m² | 16
| 8.4.3 | Strength of Concrete: 15/19
5.1.2.10 |  | Mass Concrete | m³ | 3
5.1.2.11 | 8.4.2 | Blinding layer 50mm thick | m² | 25
| 8.4.3 | Strength of Concrete: 35/19
5.1.2.12 |  | Floors | m³ | 8
5.1.2.13 |  | Walls | m³ | 33
5.1.2.14 |  | Pipe supports | m³ | 1.5
| 8.4.4 | Unformed Surface Finishes
| 8.4.4 (a) | Wood Floated Finish
5.1.2.15 |  | Top surface of box walls | m² | 5
| 8.4.4 (b) | Steel Floated Finish
5.1.2.16 |  | Benching in boxes | m² | 20
SUB-TOTAL CARRIED FORWARD
brought forward
Sundry Items
5.1.3 |  | PRE-CAST CONCRETE
5.1.3.1 |  | Precast concrete roof slab sections (1280mm x 2000mm x 300mm) (including lockable access hatch and holding brackets) as per drawing 13214-73-04-011: Scourbox Layout | No. | 1
5.1.3.2 |  | Precast concrete roof slab sections (1280mm x 2000mm x 300mm) as per drawing 13214-73-04-011: Scourbox Layout | No. | 1
5.1.4 | SANS 1200HA | STRUCTURAL STEELWORK
5.1.4.1 |  | Galvanised steel cat ladder fixed with M16 chemical anchors | No. | 1
5.1.4.2 | PSHA 5.2.13 | 50 mm Galvanised open floor grating | m² | 10
5.1.4.3 |  | 50x50x5L with 150x25x3 lugs as per drawing 13214-73-04-011: Galvanised Open Grid Flooring | No | 2
Access Hatch
5.1.4.4 |  | Lockable access hatch (1535mm x 1535mm) as per drawing13214-73-04-002: Plan on Access Hatch | No. | 2
5.1.5 | PSLD | BUILDING PIPES INTO CONCRETE WORK
| 8.3 (a) | Pipes Supplied and Installed by the Contractor (Irrespective of type)
5.1.5.1 |  | 110mm | No. | 3
5.1.5.2 |  | 150mm | No. | 4
5.1.5.3 |  | 350mm | No. | 2
5.1.5.4 |  | 600mm | No. | 1
5.1.6 | SANS 1200L | PIPEWORK
| PSL 8.2.5 | PIPE SPECIALS
5.1.6.1 | 8.2.5 | Supplying, testing and installation of pipes, fittings and specials brought forward from the Scour Chamber Pipe Schedule | Sum | 1
5.2 |  | INLET FLOWMETER CHAMBER
5.2.1 | SANS 1200D | EARTHWORKS
| 8.3.3 | Restricted Excavation
| 8.3.3(a) (i) | Excavate for Restricted Foundations, Footings and Pipe Trenches in all materials and use as described for Items
5.2.1.1 |  | 0 to 2m deep | m³ | 29
5.2.1.2 |  | 2m to 4m deep | m³ | 19
5.2.1.3 |  | (b) Intermediate excavation | m³ | 51
5.2.1.4 |  | (c) Hard rock material | m³ | 21
5.2.1.5 |  | Extra over items 5.2.1.3 to 5.2.1.4 for additional excavations required by the Engineer after excavation has been completed | m³ | 35
5.2.1.6 | 8.3.6 | Overhaul | m³.km | 50
5.2.2 | SANS 1200G | CONCRETE (STRUCTURAL)
| 8.2 | Formwork
| 8.2.2 | Smooth Formwork
Plane Vertical
5.2.2.1 |  | Internal & external sides of inlet flowmeter chamber walls | m² | 86
SUB-TOTAL CARRIED FORWARD
brought forward
5.2.2.2 |  | Sides of valve supports | m² | 1
Plane Horizontal
| PSG 8.2.6 | Box Out Holes/Form Voids
| PSG 8.2.6(a) | Circular holes for pipes
5.2.2.3 |  | 500mm | No. | 2
| PSG 8.2.7 | Chamfers larger than 20mm x 20mm
5.2.2.4 |  | 25 x 25 mm along flow meter chamber concrete cover | m | 35
| 8.3 | Reinforcement
5.2.2.5 | 8.3.1 | High tensile steel bars | t | 2
5.2.2.6 | 8.3.1 | Mild steel reinforcement | t | 0.7
| 8.3.2 | High Tensile Welded Mesh
5.2.2.7 |  | Ref. 245 for flow meter chamber cover | m2 | 5
| 8.4 | Concrete
| 8.4.3 | Strength of Concrete: 15/19
5.2.2.8 |  | Benching to floors of boxes | m² | 8
| 8.4.3 | Strength of Concrete: 15/19
5.2.2.9 | 8.4.2 | Blinding layer 50mm thick | m² | 15
| 8.4.3 | Strength of Concrete: 35/19
5.2.2.10 |  | Floors | m³ | 5
5.2.2.11 |  | Walls | m³ | 14
5.2.2.12 |  | Pipe supports | m³ | 0.05
5.2.2.13 |  | 500x500x300 deep sump | m³ | 5
| 8.4.4 | Unformed Surface Finishes
| 8.4.4 (a) | Wood Floated Finish
5.2.2.14 |  | Top surface of box walls | m² | 5
| 8.4.4 (b) | Steel Floated Finish
5.2.2.15 |  | Benching in boxes | m² | 8
Sundry Items
5.2.3 |  | PRE-CAST CONCRETE
5.2.3.1 |  | Precast concrete roof slab sections (including lockable access hatch and holding brackets) as per drawing 13214-73-04-005 | No. | 1
5.2.4 | SANS 1200HA | STRUCTURAL STEELWORK
5.2.4.1 |  | Galvanised steel ladder fixed with M16 chemical anchors | No. | 1
5.2.5 | PSLD | BUILDING PIPES INTO CONCRETE WORK
| 8.3 (a) | Pipes Supplied and Installed by the Contractor (Irrespective of type)
5.2.5.1 |  | 500 mm diameter | No. | 2
SUB-TOTAL CARRIED FORWARD
brought forward
5.2.6 | SANS 1200L | PIPEWORK
| PSL 8.2.5 | PIPE SPECIALS
5.2.6.1 |  | Supplying, testing and installation of pipes, fittings and specials brought forward from the Inlet Flow Meter Chamber Pipe Schedule | Sum | 1
5.3 |  | OUTLET FLOWMETER CHAMBER
5.3.1 | SANS 1200D | EARTHWORKS
| 8.3.3 | Restricted Excavation
| 8.3.3(a) (i) | Excavate for Restricted Foundations, Footings and Pipe Trenches in all materials and use as described for Items
5.3.1.1 |  | (a) Soft excavation | m³ | 25
5.3.1.2 |  | (b) Intermediate excavation | m³ | 12
5.3.1.3 |  | (c) Hard rock material | m³ | 9
5.3.1.4 |  | Extra over items 5.3.1.1 to 5.3.1.3 for additional excavations required by the Engineer after excavation has been completed | m³ | 35
5.3.1.5 | 8.3.6 | Overhaul | m³.km | 100
5.3.2 | SANS 1200G | CONCRETE (STRUCTURAL)
| 8.2 | Formwork
| 8.2.2 | Smooth Formwork
Plane Vertical
5.3.2.1 |  | Internal & external sides of inlet chamber walls | m² | 95
5.3.2.2 |  | Sides of valve supports | m² | 1
| PSG 8.2.7 | Chamfers larger than 20mm x 20mm
5.3.2.3 |  | 25 x 25 mm along flow meter chamber concrete cover | m | 35
| 8.3 | Reinforcement
5.3.2.4 | 8.3.1 | High tensile steel bars | t | 2.205
5.3.2.5 | 8.3.1 | Mild steel bars | t | 0.882
| 8.3.2 | High Tensile Welded Mesh
5.3.2.6 |  | Ref. 245 for flow meter chamber cover | m2 | 5
| 8.4 | Concrete
| 8.4.3 | Strength of Concrete: 15/10
5.3.2.7 |  | Benching to floors of boxes | m² | 8
| 8.4.3 | Strength of Concrete: 15/19
5.3.2.8 | 8.4.2 | Blinding layer 50mm thick | m² | 15
| 8.4.3 | Strength of Concrete: 35/19
5.3.2.9 |  | Floors | m³ | 5
5.3.2.10 |  | Walls | m³ | 15
5.3.2.11 |  | Pipe supports | m³ | 0.05
5.3.2.12 |  | 500x500x300 deep sump | m³ | 5
| 8.4.4 | Unformed Surface Finishes
| 8.4.4 (a) | Wood Floated Finish
SUB-TOTAL CARRIED FORWARD
brought forward
5.3.2.13 |  | Top surface of box walls | m² | 5
| 8.4.4 (b) | Steel Floated Finish
5.3.2.14 |  | Benching in boxes | m² | 8
Sundry Items
5.3.3 |  | PRE-CAST CONCRETE
5.3.3.1 |  | Precast concrete roof slab sections (including lockable access hatch and holding brackets) as per drawing 13214-73-04-005 | No. | 1
5.3.4 | SANS 1200HA | STRUCTURAL STEELWORK
5.3.4.1 |  | Galvanised steel ladder fixed with M16 chemical anchors | No. | 1
5.3.5 | PSLD | BUILDING PIPES INTO CONCRETE WORK
| 8.3 (a) | Pipes Supplied and Installed by the Contractor (Irrespective of type)
5.3.5.1 |  | 600 mm diameter | No. | 2
5.3.6 | SANS 1200L | PIPEWORK
| PSL 8.2.5 | PIPE SPECIALS
5.3.6.1 |  | Supplying, testing and installation of pipes, fittings and specials brought forward from the Inlet Flow Meter Chamber Pipe Schedule | Sum | 1
5.4 |  | DRAINAGE BOXES
5.4.1 | SANS 1200D | EARTHWORKS
| 8.3.3 | Restricted Excavation
| 8.3.3(a) (i) | Excavate for Restricted Foundations, Footings and Pipe Trenches in all materials and use as described for Items
5.4.1.1 |  | (i)(a) 0 m up to 2 m | m³ | 86
| 8.3.2(b) | Extra Over Items for Excavations in:
5.4.1.2 |  | (a) Intermediate excavation | m³ | 30
5.4.1.3 |  | (b) Hard rock material | m³ | 27
5.4.1.4 |  | Extra over items 5.4.1.2 to 5.4.1.3 for additional excavations required by the Engineer after excavation has been completed | m³ | 35
5.4.2 | SANS 1200G | CONCRETE (STRUCTURAL)
| 8.2 | Formwork
| 8.2.2 | Smooth Formwork
Plane Vertical
5.4.2.1 |  | Internal & external sides of drainage chamber walls | m² | 360
| PSG 8.2.7 | Chamfers larger than 20mm x 20mm
5.4.2.2 |  | 25 x 25 mm along wall edge of drainage boxes | m | 135
| 8.3 | Reinforcement
5.4.2.3 | 8.3.1 | High tensile steel bars | t | 20
5.4.2.4 | 8.3.1 | Mild steel bars | t | 6
| 8.4 | Concrete
| 8.4.3 | Strength of Concrete: 15/10
5.4.2.5 |  | Benching to floors of boxes | m² | 24
SUB-TOTAL CARRIED FORWARD
brought forward
| 8.4.3 | Strength of Concrete: 15/19
5.4.2.6 | 8.4.2 | Blinding layer 50mm thick | m² | 40
| 8.4.3 | Strength of Concrete: 35/19
5.4.2.7 |  | Floors | m³ | 8
5.4.2.8 |  | Walls | m³ | 32
| 8.4.4 | Unformed Surface Finishes
| 8.4.4 (a) | Wood Floated Finish
5.4.2.9 |  | Top surface of box walls | m² | 16
| 8.4.4 (b) | Steel Floated Finish
5.4.2.10 |  | Benching in boxes | m² | 24
Sundry Items
5.4.3 | SANS 1200HA | STRUCTURAL STEELWORK
5.4.3.1 |  | Grade 304 Stainless Steel 900mm x 900mm frame to be cast into concrete walls of boxes | No. | 12
5.4.4 |  | GRP Products
5.4.4.1 |  | GRP grating to fit inside item 5.4.3.1 | No. | 12
5.4.4 | PSLD | BUILDING PIPES INTO CONCRETE WORK
| 8.3 (a) | Pipes Supplied and Installed by the Contractor (Irrespective of type)
5.4.4.1 |  | 50 mm diameter | No. | 48
5.4.4.2 |  | 110 mm diameter | No. | 24
5.5 |  | VALVE CHAMBERS
5.5.1 | SANS 1200D | EARTHWORKS
| 8.3.3 | Restricted Excavation
| 8.3.3(a) (i) | Excavate for Restricted Foundations, Footings and Pipe Trenches in all materials and use as described for Items
5.5.1.1 |  | (a) Soft excavation | m³ | 22
5.5.1.2 |  | (b) Intermediate excavation | m³ | 37
5.5.1.3 |  | (c) Hard rock material | m³ | 15
5.5.1.4 |  | Extra over items 5.3.1.1 to 5.3.1.3 for additional excavations required by the Engineer after excavation has been completed | m³ | 70
5.5.1.5 | 8.3.6 | Overhaul | m³.km | 200
5.5.2 | SANS 1200G | CONCRETE (STRUCTURAL)
| 8.2 | Formwork
| 8.2.2 | Smooth Formwork
Plane Vertical
5.5.2.1 |  | Internal & external sides of inlet chamber walls | m² | 190
5.5.2.2 |  | Sides of valve supports | m² | 2
| PSG 8.2.7 | Chamfers larger than 20mm x 20mm
5.5.2.3 |  | 25 x 25 mm along valve chamber concrete cover | m | 65
SUB-TOTAL CARRIED FORWARD
brought forward
| 8.3 | Reinforcement
5.5.2.4 | 8.3.1 | High tensile steel bars | t | 4.41
5.5.2.5 | 8.3.1 | Mild steel bars | t | 1.764
| 8.3.2 | High Tensile Welded Mesh
5.5.2.6 |  | Ref. 245 for flow meter chamber cover | m2 | 10
| 8.4 | Concrete
| 8.4.3 | Strength of Concrete: 15/10
5.5.2.7 |  | Benching to floors of boxes | m² | 16
| 8.4.3 | Strength of Concrete: 15/19
5.5.2.8 | 8.4.2 | Blinding layer 50mm thick | m² | 30
| 8.4.3 | Strength of Concrete: 35/19
5.5.2.9 |  | Floors | m³ | 10
5.5.2.10 |  | Walls | m³ | 30
5.5.2.11 |  | Pipe supports | m³ | 0.1
5.5.2.12 |  | 500x500x300 deep sump | m³ | 5
| 8.4.4 | Unformed Surface Finishes
| 8.4.4 (a) | Wood Floated Finish
5.5.2.13 |  | Top surface of box walls | m² | 10
| 8.4.4 (b) | Steel Floated Finish
5.5.2.14 |  | Benching in boxes | m² | 16
Sundry Items
5.5.3 |  | PRE-CAST CONCRETE
5.5.3.1 |  | Precast concrete roof slab sections (including lockable access hatch and holding brackets) as per drawing 13214-73-04-005 | No. | 2
5.5.4 | SANS 1200HA | STRUCTURAL STEELWORK
5.5.4.1 |  | Galvanised steel ladder fixed with M16 chemical anchors | No. | 2
5.5.5 | PSLD | BUILDING PIPES INTO CONCRETE WORK
| 8.3 (a) | Pipes Supplied and Installed by the Contractor (Irrespective of type)
5.5.5.1 |  | 500 mm diameter | No. | 2
5.5.5.2 |  | 600 mm diameter | No. | 2
5.5.6 | SANS 1200L | PIPEWORK
| PSL 8.2.5 | PIPE SPECIALS
5.5.6.1 |  | Supplying, testing and installation of pipes, fittings and specials brought forward from the Inlet Flow Meter Chamber Pipe Schedule | Sum | 1
TOTAL FOR SECTION 5 (Carried to Summary)
Note on C170: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: water tightness not a problem? No cast in flanges? Reply: There are cast in flanges. Must we make the diameter bigger to account for this?

## 6.Interconnecting Pipework
SECTION 6: INTERCONNECTING PIPEWORK
ITEM NO | PAYMENT CLAUSE | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
Formatting to be fixed
SECTION 6: INTERCONNECTING PIPEWORK
Piping config to be confirmed
6.1 | SANS 1200DB | PIPE TRENCHES |  |  |  |  | Levels to be confirmed and updated
Piping config to be confirmed
|  | Excavation |  |  |  |  | Valves & Pipe Specials to be confirmed
Revise concrete grades as per EFM Spec
| 8.3.2 | Excavate in all materials For Trenches, Backfill and Compact, including Disposal of Surplus Unsuitable Maternal for Pipes
Up to 300 mm Diameter for depths
6.1.1 |  | 0.0 m - 1.0 m | m | 47.5
6.1.2 |  | 1.0 m - 2.0 m | m | 84.5
6.1.3 |  | 2.0 m - 3.0 m | m | 178
Over 300mm up tp 600 mm diameter for depths
6.1.4 |  | 0.0 m - 1.0 m | m | 150
6.1.5 |  | 1.0 m - 2.0 m | m | 150
6.1.6 |  | 2.0 m - 3.0 m | m | 88
6.1.7 |  | 3.0 m - 4.0 m | m | 10
| 8.3.2 (b) | Extra Over items 6.1.1 to 6.1.7 for excavations
6.1.8 | 8.3.2 (I) | Intermediate material | m3 | 366
6.1.9 | 8.3.2 (ii) | Hard rock material | m3 | 237.5
| 8.3.3 | Excavation Ancillaries
6.1.10 | 8.3.3.3 | Compaction in road reserve (provisional) | m³ | 10
6.1.11 | 8.3.3.4 | Overhaul | m³.km | 50
| PSDB 8.3.5 | Existing Services that Intersect or Adjoin of a Pipe Trench
6.1.12 |  | (a) Services that intersect with the trench | No. | 10
6.1.13 |  | (b) Services that adjoin a trench | m | 50
| 8.3.6 | Finishing
6.1.14 | 8.3.6.1 | (a) Reinstate road surface complete with all courses at pipe crossings | m² | 50
6.1.15 | 8.3.7 | Accommodation of Traffic | Sum | 1
6.2 | SANS 1200L | MEDIUM PRESSURE PIPEWORK
| 8.2.1 | Interconnecting Pipework
Supply, lay, join and test pipework on granular bedding
6.2.1 |  | 50 mm diameter PVC drainage pipe in concrete | m | 75
6.2.2 |  | 50 mm diameter PE100PN10 HDPE pipe | m | 50
6.2.3 |  | 75 mm diameter PVC perforated drainage in no fines concrete | m | 310
6.2.4 | PSLE 8. | 110 mm diameter PVC perforated drainage pipe in no fines concrete | m | 340
| PSL 8.2.5 | Pipe Specials
6.2.5 |  | Supply, testing and installation of pipework, fittings and specials brought forward from the Pipe Schedule for the Inlet Pipe (building in of pipes measured elsewhere) | Sum | 1 |  |  | The correct wording for this item is …... And it is for the total amount in the pipe schedule for this section | Supplying, testing and installation of pipes, fittings and specials brought forward from the Pipe Schedule
SUB-TOTAL CARRIED FORWARD
6.2.6 |  | Supply, testing and installation of pipework, fittings and specials brought forward from the Pipe Schedule for the Oulet Pipe (building in of pipes measured elsewhere) | Sum | 1 |  |  | The correct wording for this item is …... And it is for the total amount in the pipe schedule for this section | Supplying, testing and installation of pipes, fittings and specials brought forward from the Pipe Schedule
| 8.2.11 | Thrust Blocks
6.2.7 |  | Concrete grade 15/20 in thrust blocks (per Employer's Agent instruction) | m³ | 10
6.2.8 |  | Rough shuttering at thrust blocks (per Employer's Agent's instruction) | m² | 50
6.3 | SANS 1200LB | BEDDING
| 8.2.2.1 | Provision of bedding material from trench or other excavations within freehaul distance
6.3.1 | (a) | Selected granular material | m3 | 86
6.3.2 | (b) | Selected fill blanket | m3 | 120
| 8.2.2.3 | Provision of bedding material by importation from commercial sources.
6.3.3 | (a) | Selected granular material | m3 | 86
6.3.4 | (b) | Selected fill blanket | m3 | 120
| 8.2.4 | Concrete at Pipes
6.3.5 |  | Encasing of 110mm dia underfloor drainage pipes in concrete | m³ | 60
6.3.6 |  | Encasing of 150mm dia drainage & scour pipes in concrete | m³ | 8
6.3.7 |  | Encasing of 350mm dia overflow pipe in concrete | m³ | 4
6.3.8 |  | Encasing of 500mm dia inlet pipe in concrete | m³ | 10
6.3.9 |  | Encasing of 600mm dia outlet pipe in concrete | m³ | 15
6.4 | SANS 1200LG | PIPE JACKING
| 8.2.6 | Supply and install pipes by pipe jacking method, complete with excavations
6.4.1 |  | for 500mm steel pipe | m | 20
6.4.2 |  | for 600mm steel pipe | m | 21
SEWERS
6.5 | SANS 1200DB | Excavation
| PSD 8.3.3 (a) | Excavate in all materials for backfill, compact and dispose of material |  |  |  |  | state for pipe sizes
6.5.1 |  | 0m - 2m | m³ | 639
| PSD 8.3.3 (b) | Extra-over items for excavating in
6.5.2 |  | Intermediate material | m3 | 383.4
6.5.3 |  | Hard rock material | m3 | 255.6
6.5.4 |  | Extra over items 6.5.1 to 6.5.3 for additional excavations required by the Employer's Agent after excavation has been completed | m³ | 90 |  |  | >> Add: Additional Excavation as insructed by the Employer's Agent
6.6 | SANS 1200LB | BEDDING
| 8.2.2.1 | Provision of Bedding Material from Trench or Other Excavations within Freehaul Distance
6.6.1 | (a) | Selected granular material | m3 | 70
SUB-TOTAL CARRIED FORWARD
brought forward
| 8.2.2.3 | Provision of bedding material by importation from commercial sources |  |  |  |  | Add these items
6.6.3 | (a) | Selected granular material | m3 | 20
6.6.4 | (b) | Selected fill blanket | m3 | 30
6.6.5 | 8.2.3 | Grade 20/19 concrete in bedding cradle | m3 | 50
6.7 | SANS 1200LD | SEWER RETICULATION
| 8.2.1 | Supply, Lay, Joint and test uPVC Pipes
6.7.1 |  | 50 mm diameter uPVC basin drain from guard house | m | 100
6.7.2 |  | 110 mm diameter PVC sewer drainage pipe connecting from guard house | m | 800
6.7.3 |  | 200 mm diameter uPVC sewer drainage pipe connecting from guard house | m | 750
Manholes
| 8.2.3 | Manholes 1250 mm inside diameter complete with concrete base, type 4 cover and frame, for depths
6.7.4 |  | 0.5 m - 1.0 m | No. | 2
6.7.5 |  | 1.0 m - 1.5 m | No. | 2
|  | Extra over for type 2A manhole cover and frame | No. | 2
| (a) | Services that Intersect a pipe trench
6.7.6 |  | Electrical cables (irrespective of diameter) | No. | 2
6.7.7 |  | Pipeline (irrespective of diameter) | No. | 2
| (b) | Services that adjoin a pipe trench
6.7.8 |  | Pipeline (irrespective of diameter) | m | 100
6.7.9 | 8.2.7 | Encasement of pipes in class 15/20 concrete where directed by the Employer's Agent only | m3 | 25
| 8.2.11 | Connection Existing Sewer Line
6.7.10 |  | Tie into exisiting 500 dia. pipe | Sum | 1
6.7.11 |  | Tie into exisiting 600 dia. pipe | Sum | 1
6.7.12 | 8.2.12 | Raising or lowering of existing manholes | No | 4
|  | Building Pipes into Brickwork | [5 empty] | >> Building in of sewer into brickwork -PSLD 8.3
| 8.4 | SUPPLYING AND BUILDING HDPE OR uPVC PIPES AS SPECIFIED INTO BRICKWORK (FOR CABLE SLEEVES OR PIPE SLEEVES)
6.7.13 |  | 50 mm dia. uPVC Tee piece | No. | 2
6.7.14 |  | 110 mm dia. uPVC Tee piece | No. | 2
TOTAL FOR SECTION 6 (Carried to Summary)
Note on C12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Shoring included? Reply: This is covered in SANS 1200D, 5.1. The contractor is instructed to include brace the sides of excavations in this clause so i believe it is covered. Clause 8.3.2 of SANS1200DB refrences CLause 5.1 which in turn refrences SANS 1200D, 5.1

## 7. Guard House
SECTION 7: GUARD HOUSE
ITEM NO | PAYMENT CLAUSE | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
SECTION 7: GUARD HOUSE
7.1 | SANS 1200 D | EARTHWORKS
Restricted Excavation
| 8.3.3 | Excavate for restricted foundations, footings and pipe trenches in all materials and use for backfill or embankment or dispose
7.1.1 |  | Strip Footings | m³ | 12
|  | Apron Slab | m³ | 1.5
| PSD 8.3.3 (b) | Extra-over items for excavating in
7.1.2 |  | Intermediate material | m3 | 213
7.1.3 |  | Hard rock material | m3 | 213
7.1.4 |  | Extra over items 7.1.2 to 7.1.4 for additional excavations required by the Engineer after excavation has been completed | m³ | 90 |  |  | >> Add: Additional Excavation as insructed by the engineer
7.1.5 | 8.3.6 | Overhaul | m³.km | 250
7.2 | SANS 1200G | CONCRETE (STRUCTURAL)
| 8.2 | Formwork
| 8.2.1 | Rough Formwork
Plane Vertical
7.2.1 |  | Sides of Footings | m² | 6.8775
| 8.2.2 | Smooth Formwork
Plane Vertical
7.2.2 |  | Edge of roof slab | m² | 6.8775
7.2.3 |  | Edge of apron slab (80mm thick) | m² | 2
Plane Horizontal
7.2.4 |  | Soffit of Roof slab | m2 | 18.4
| PSG 8.3 | Reinforcement
7.2.5 |  | High tensile steel bars | t | 0.21 |  |  | >> High Tensile + Mild Steel
7.2.6 |  | Mild steel bars | t | 0.063
High Tensile Welded Mesh
7.2.7 |  | Ref. 245 for floor slabs | m2 | 8
7.2.8 |  | Ref. 193 for apron slabs | m2 | 23 |  |  | swop the two types
| 8.1.3 | Concrete
| 8.4.2 | Blinding Layer in Grade 15/19 concrete with 50mm thickness
7.2.9 |  | Underneath footing | m2 | 12 |  |  | Building floor slabs normally only have plastic not blinding
Strength Concrete 25/19
7.2.10 |  | Strip footing (600 mm wide, 250 mm thick) | m3 | 10
7.2.11 |  | Floor slab | m3 | 10
7.2.12 |  | Apron Slabs (80mm thick) | m3 | 2
| 8.4.4 a) | Wood float finish for upper surfaces of:
7.2.13 |  | Top of floors and apron slabs | m2 | 25
SUB-TOTAL CARRIED FORWARD
| 8.5 | Joints
| 8.5.2 | Filled Joints
Joint filler consisting of closed cell expanded polyethylene with density not less than 120kg/m3 including bullnose finish to both sides of joint and tear off strip
7.2.14 |  | 10 mm wide between 100 mm concrete apron | m | 1.1314
7.2.15 |  | 20 mm wide between concrete and brickwork | m | 40
| 8.5.3 | Sealed Joints
Joint sealer (20 x 15 mm) consisting of a two component polyether based polyurethane sealing compound on visible face of joint including primer and bond breaker
7.2.16 |  | 20 mm joint between brick and concrete | m | 39.43
| PSU | Building Work
7.3 | PSU 8.8 | IRONMONGERY
Doors and Windows
Steel doors, frames and windows (as per schedule on drawing 13214-73-04-003)
7.3.1 | PSU 8.8.1 (b) | 1000mm x 2000mm High Single Panel Steel Combination Door & Frame | No. | 1
7.3.2 | PSU 8.8.3 | 1000mm x 2000mm High Single Panel Steel Security Gate. | No. | 1
7.3.3 |  | 800mm x 2100mm High standard semi-solid door to be supplied with frame, cabin hook and a level 3 lock set complete with two keys. All fittings, door restraints and hinges solid brass | No. | 1
7.3.4 |  | 1020mm x 950mm Windows SSF43 with burglar proofing | No. | 3
7.3.5 |  | 410mm x 610mm - M fixed with trim. Including 12mm diameter MS burglar proofing on full face of window, glazed and painted to system A2. | No. | 1
7.3.6 | PSU 8.15 (b) | Painting of doors and windows | No. | 2
7.3.7 | PSU 8.15 (c) | Painting of windows | No. | 3
7.4 | PSLE | POLYETHYLENE SHEETING
7.4.1 | 8.2.18 | 250 micron polyethylene underneath strip footing and floor slab including ANT poison to SANS 618 | m² | 10
Brickwork
7.4.2 | PSU 8.1 (b) | 230mm thick, both faces, 14 MPa face brick Exterior wall including brick force | m2 | 5
7.4.3 | PSU 8.1 (c) | 115mm thick, 14 MPa face brick Interior Wall including brick force | m2 | 5
7.5 |  | GENERAL - FIXTURES
7.5.1 |  | Installation of Wall Mounted Wash basin with Basin Taps | No. | 1
7.5.2 |  | Installation of Front Flush Toilet Suite | No. | 1
EXISTING SERVICES
7.5.3 |  | Water supply to guard house | Sum | 1 |  |  | >> Variation to drawings - We need to change the line to connect to the reservoir
TOTAL FOR SECTION 7 (Carried to Summary)
Note on C34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: What about formwork for slab joints eg apron slab? Reply: doesn't appear to be included. drawing doesnt include apron slab, hence it was not measured.
Note on C36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not cast against? Reply: Should i remove this?
Note on C64: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 19mm stone ie 15/19
Note on C104: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: doors, windows not structural steel Reply: Replaced with PSU 8.8
Note on C106: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: doors and windows are not classed as structural steel. they fall under iron mongery Reply: As above

## 8. Telemetry Hut
SECTION 8: TELEMETRY HUT
ITEM NO | PAYMENT CLAUSE | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
SECTION 8: TELEMETRY HUT
8.1 | SANS1200D | EARTHWORKS
| 8.3.3 | Restricted Excavation
| 8.3.3 a) | Excavate for restricted foundations, footings and pipe trenches in all materials and use for backfill or embankment or dispose
8.1.1 |  | Footings | m³ | 7.5
8.1.2 |  | Apron Slab | m³ | 1.5
| PSD 8.3.3 (b) | Extra-over items for excavating in
8.1.3 |  | Intermediate material | m3 | 7.5
8.1.4 |  | Hard rock material | m3 | 6
8.1.5 |  | Extra over items 8.1.1 to 8.1.3 for additional excavations required by the Engineer after excavation has been completed | m³ | 5.5 |  |  | >> Add: Additional Excavation as insructed by the engineer
>> Ensure items are same as he Guard house - comments apply
8.1.6 | 8.3.6 | Overhaul | m³.km | 250
8.2 | SANS 1200G | CONCRETE (STRUCTURAL) | [7 empty] | 1215
| 8.2 | Formwork
| 8.2.1 | Rough Formwork
|  | Plane Vertical | [6 empty] | 2.54
10.16
8.2.1 |  | Sides of Footings | m² | 5
8.2.2 |  | Edge of apron slab (80mm thick) | m² | 2
Plane Horizontal
8.2.3 |  | Soffit of Roof slab | m² | 16
| 8.2.5 | Narrow width (up to 300mm wide)
8.2.4 |  | Sides of floor slabs | m | 11
8.2.5 |  | Sides of roof slab | m | 16
| PSG 8.2.6 | Box Out Holes/Form Voids
| PSG 8.2.6 (a) | Cylindrical Openings with Volume
Over and up to and Including
8.2.6 |  | (ii) 0,01-0,05 m³ | No. | 4
| PSG 8.2.7 | Chamfers larger than 20mm x 20mm
8.2.7 |  | 25 mm along edge of roof | m | 25
| 8.3.2 | High Tensile Welded Mesh
8.2.8 |  | Ref. 245 for floor slabs | m2 | 10
8.2.9 |  | Ref. 193 for apron slabs | m2 | 16 |  |  |  | 2.8728
| 8.1.3 | Concrete
| PSG 8.4.3 | Strength of Concrete: 15/19
8.2.10 | 8.4.2 | Blinding layer 50mm thick under footing (horizontal) | m² | 10 |  |  | 592.5095 |  | >> Add blinding undert reservoir footing to this figure
Strength Concrete : 25/19
8.2.11 |  | Strip footing (650 mm wide, 250 mm thick) | m3 | 5
8.2.12 |  | Apron Slabs (80mm thick) | m3 | 2
SUB-TOTAL CARRIED FORWARD
brought forward
8.2.13 |  | Floor slab | m3 | 2
8.2.14 |  | Roof | m3 | 3.5
| 8.4.4 a) | Wood float finish for upper surfaces of:
8.2.15 |  | Floor Slab | m2 | 10
8.2.16 |  | Apron Slab | m2 | 16
| PSG 8.5 | Joints
8.2.17 |  | 10 mm Joint with approved polysulphide sealant as per drawing 13214-73-005-001 | m | 10
| 8.5.2 | Filled Joints
Joint filler consisting of closed cell expanded polyethylene with density not less than 120kg/m3 including bullnose finish to both sides of joint and tear off strip
8.2.18 |  | 20 mm wide between concrete members | m | 5
8.2.19 |  | 20 mm wide between concrete and brickwork | m | 35
| 8.5.3 | Sealed Joints
Joint sealer (20 x 15 mm) consisting of a two component polyether based polyurethane sealing compound on visible face of joint including primer and bond breaker
8.2.20 |  | 20 mm joint between brick and concrete | m | 32.16
Building Work
8.3 | PSLE | POLYETHYLENE SHEETING
8.31 | 8.2.18 | 250 micron polyethylene underneath strip footing and floor slab including ANT poison to SANS 618 | m² | 10
8.3.2 |  | DPC as specified by the employer's agent | m² | 5
8.4 | PSU | BRICKWORK
8.4.1 | PSU 8.1 (b) | 230mm thick, both faces, 14 MPa face brick including brick force | m2 | 5
| PSU 8.8 | Ironmongery
| PSU 8.8.1 | Doors and Windows
Steel doors, frames and windows (as per schedule on drawings 13214-73-05-001: Doors)
8.4.2 | PSU 8.8.1 (b) | 900mm x 2100mm High Single Panel Steel Combination Door & Frame | No. | 1
8.4.3 | PSU 8.8.3 | 1000mm x 2000mm High Single Panel Steel Security Gate. | No. | 1
TOTAL FOR SECTION 8 (Carried to Summary)
Note on C124: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: strength , type - eg 14MPa face or 7MPa stock Reply: I'm assuming 14Mpa since facebrick? not included in spec

## 9. Valve Building
SECTION 9: VALVE BUILDING
ITEM NO | PAYMENT CLAUSE | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
SECTION 9: VALVE BUILDING
9.1 | SANS1200D | EARTHWORKS
| PSD 8.3.3 | Restricted Excavation
| PSD 8.3.3 (a) | Excavate for restricted foundations, footings and pipe trenches in all materials and use for backfill or embankment or dispose
9.1.1 |  | 0 to 2m deep | m³ | 320
9.1.2 |  | 2m to 4m deep | m³ | 265
| PSD 8.3.3 (b) | Extra over items 9.1.1 to 9.1.2 for
9.1.3 |  | Soft material | m3 | 280 |  |  | >> Specify the depths 0-2, 2-4
9.1.4 |  | Intermediate material | m3 | 122.5
9.1.5 |  | Hard rock material | m3 | 132.8
9.1.6 |  | Extra over items 9.1.3 to 9.1.5 for additional excavations required by the Engineer after excavation has been completed |  |  |  |  | >> Add: Additional Excavation as insructed by the engineer
9.1.7 | 8.3.3.4 | Overhaul | m³.km | 250
| PSLD | Building Pipes into Concrete Work
| 8.3(a) | Pipes Supplied and Installed by the Contractor (Irrespective of type)
9.1.8 |  | 500mm Stainless Steel Inlet | No | 2
9.1.9 |  | 600mm Stainless Steel Outlet | No | 2
| SANS 1200L | PIPEWORK
| PSL 8.2.5 | Pipe Specials
9.1.10 |  | Supply, testing and installation of pipework, fittings and specials brought forward from the Pipe Schedule for the Valve Building (building in of pipes measured elsewhere) | Sum | 1 |  |  | The correct wording for this item is …... And it is for the total amount in the pipe schedule for this section
9.2 | SANS 1200G | CONCRETE (STRUCTURAL)
| 8.2 | Formwork
Smooth Formwork
Plane Vertical
9.2.1 |  | Edge of floor slab | m² | 320 |  |  | 317
9.2.2 |  | Internal & External Sump walls | m² | 8 |  |  | 3.36
9.2.3 |  | Internal & External valve building walls | m² | 302
9.2.4 |  | Edge of walkway | m² | 15 |  |  | 5.7112
9.2.5 |  | Sides of stairs | m² | 5 |  |  | 3
9.2.6 |  | Risers of stairs | m² | 5
9.2.7 |  | Columns | m² | 67.2
9.2.8 |  | Ring beam | m² | 80.92 |  |  | 59.04
9.2.9 |  | Support beam | m² | 161.84 |  |  | 60.624
9.2.10 |  | Edge of concrete roof | m² | 15.45 |  |  | 25
9.2.11 |  | Pipe supports | m² | 14 |  |  | 14
SUB-TOTAL CARRIED FORWARD
brought forward
Plane Horizontal
9.2.12 |  | Soffit of walkway | m² | 25 |  |  | 24
9.2.13 |  | Soffit of ring beams | m² | 15 |  |  | 12
9.2.14 |  | Soffit of support beams | m² | 15 |  |  | 12
9.2.15 |  | Soffit of roof | m² | 253.68 |  |  | 186
Plane Sloping
7
9.2.16 |  | Soffit of staircase | m² | 7
| PSG 8.2.7 | Chamfers larger than 20mm x 20mm
9.2.17 |  | 25 mm along edge of roof | m | 125
| 8.4 | Concrete
| 8.4.3 | Strength of Concrete: 15/19
9.2.18 |  | Screed on top of floor | m² | 160
| 8.4.3 | Strength of Concrete: 15/19
9.2.19 |  | Blinding layer 50mm thick | m² | 160
Strength of Concrete: 25/19
9.2.20 |  | Apron | m³ | 15 |  |  | >> Concrete class should be 20/20
| 8.4.3 | Strength of Concrete: 35/19
9.2.21 |  | Floor | m³ | 80 |  |  | 55
9.2.22 |  | Walls | m³ | 65 |  |  | 49
9.2.23 |  | Pipe supports | m³ | 5 |  |  | 2
9.2.24 |  | Walkway | m³ | 15 |  |  | 7.074
9.2.25 |  | Stairs | m³ | 2
9.2.26 |  | Columns | m³ | 5 |  |  | 2.304
9.2.27 |  | Ring beams | m³ | 10
9.2.28 |  | Support beams | m³ | 20
9.2.29 |  | Roof | m³ | 59.43
57
9.2.30 |  | Concrete Sump | m³ | 5
9.2.31 | 8.3 | Reinforcement
9.2.32 | 8.3.1 | High Tensile Reinforced Bars | t | 15
9.2.33 |  | Mild Steel Reinforced to Structural Concrete Work | t | 5
| 8.4.4 | Unformed Surface Finishes
| 8.4.4 (a) | Wood Floated Finish
9.2.34 |  | Top of floor | m² | 160
9.2.35 |  | Top of walkway | m² | 30
9.2.36 |  | Treads of stairs | m² | 5
| 8.5 | Joints
| 8.5.2 | Filled Joints (Including Formwork)
SUB-TOTAL CARRIED FORWARD
brought forward
Joint Filler Consisting of Closed Cell Expanded Polyethylene with Density not less than 120 kg/m3 including Bullnose Finish to both sides of Joint.
9.2.37 |  | 20 mm wide between 100 mm concrete apron | m | 13.6144
9.3 | SANS 1200HA | STRUCTURAL STEELWORK (SUNDRY ITEMS)
| 8.3.1 | Crawl Beam
Supply and Installation of 254x146x31 kg/m Galvanized M.S I-Beam complete with stops ends, etc. All as shown on drawing 13214-73-05-006, including testing and a certificate proving compliance with the requirements of the department of labour
9.3.1 |  | 14 700 mm long | No. | 2
9.3.2 |  | M20 galvanized cast in U-bolts complete with spacers, washers and nuts and M20 anchor bars for fixing of crawl beam | No. | 32
| PSHA 8.3.2(b) | Handrail Assembly Complete
9.3.3 |  | Supply and installation of complete 3CR12 stainless steel handrail assembly | m | 35
9.4 | PSU | BUILDING WORK
| 8.1 | Brickwork
9.4.1 | PSU 8.1 (b) | 230mm thick, both faces, 7MPa face brick including brick force and damp proofing | m² | 306
Air Bricks
9.4.2 |  | 170 mm x 170 mm Standard vermin proof air bricks | No. | 4
9.5 | PSU 8.6 | WATERPROOFING OF CONCRETE ROOFS
9.5.1 |  | Valve Building | Sum | 1
9.6 | PSU 8.8 | IRONMONGREY
| PSU 8.8.1 | Steel doors, frames and windows (as per schedule on drawings 13214-73-05-005)
9.6.1 | PSU 8.8.1 (b) | D2 standard single steel door and frame (940 wide x 2 134 mm high) | No. | 1
9.6.2 | PSU 8.8.1 (c) | Windows SS43 with burglar proofing | No. | 10
9.6.3 |  | Industrial Type Roller shutter door (3m wide x 3m high) | No. | 1
9.7 |  | WATER SAMPLING POINT
9.7.1 |  | Lockable sample box to be fixed to building as per drawing 13214-73-05-006 (700mm wide x 1200mm long x 1200mm high from 4.5mm 304 SS) | No. | 1
9.8 |  | MECHANICAL EQUIPMENT
9.8.1 |  | Underhung overhead crane to fit onto the two fixed crawl beams (item 9.3.1) 10.17m apart (motorised) | No. | 1
9.8.2 |  | Submersible pump to deliver 3 l/s at a head of 10m including 40mm dia. GMS piping inside the building | No. | 1
9.8.3 |  | Submersible pump to deliver 3 l/s at a head of 10m including 20m long 40mm dia. Flexible pipe | No. | 1
TOTAL FOR SECTION 9 (Carried to Summary)

## 10. ElectricaI and C&I
SECTION 10: ELECTRICAL AND C&I
ITEM NO | PAYMENT CLAUSE | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
SECTION 10: ELECTRICAL AND C&I
10.1 | PSY 1.2 | ELECTRICAL CALBLE RACKS
Rate to include for the Supply only of the following Plant And Equipment Including Delivery, Storage, Quality Assurance and All Necessary Insurance
Supply and Deliver Cable Ladder
10.1.1 |  | 100mm wide x 76mm | m | 30
Supply and Deliver of Horizontal Bends
10.1.2 |  | 100mm wide x 76mm | ea | 4
Supply and Deliver of Vertical Bends
10.1.3 |  | 100mm wide x 76mm | ea | 4
Supply and Deliver of Internal Bends
10.1.4 |  | 100mm wide x 76mm | ea | 4
Supply and Deliver of External Bends
10.1.5 |  | 100mm wide x 76mm | ea | 3
Supply and Deliver of Tee-Pieces
10.1.6 |  | 100mm wide x 76mm | ea | 3
Supply and Deliver of Cable Ladder Support Struts Material
10.1.7 |  | P1000 (41x41 x 2.5mm thickness) | m | 6
10.1.8 |  | P1000T (41x41 x 2.5mm thickness, slot 25x11@50centers) | m | 18
Supply and Deliver of Cable Ladder Support Cantilever Arms P1000 arm
10.1.9 |  | 150mm | ea | 4
10.1.10 |  | 200mm | ea | 8
10.1.11 |  | 250mm | ea | 2
10.2 | PSY 1.2 | Rate to include only for Installation, Commissioning, Testing And Adjusting The Following Plant and Equipment as a Completely Separate Operation Sometime after the Completion and/or Erection and Installation, Including Transportation And Accommodation for Personnel
| E02.8 | Installation of Cable Ladder
10.2.1 |  | 100mm wide x 76mm | m | 30
| E02.8 | Installation of Horizontal Bends
10.2.2 |  | 100mm wide x 76mm | ea | 4
| E02.8 | Installation of Vertical Bends
10.2.3 |  | 100mm wide x 76mm | ea | 4
| E02.8 | Installation of Internal Bends
10.2.4 |  | 100mm wide x 76mm | ea | 4
| E02.8 | Installation of External Bends
10.2.5 |  | 100mm wide x 76mm | ea | 3
SUB-TOTAL CARRIED FORWARD
brought forward
| E02.8 | Installation of Tee-Pieces
10.2.6 |  | 100mm wide x 76mm | ea | 3
| E02.8 | Installation of Cable Ladder Support Struts Material
10.2.7 |  | P1000 (41x41 x 2.5mm thickness) | m | 6
10.2.8 |  | P1000T (41x41 x 2.5mm thickness, slot 25x11@50centers) | m | 18
| E02.8 | Installation of Cable Ladder Support Cantilever Arms P1000 arm
10.2.9 |  | 150mm | ea | 4
10.2.10 |  | 200mm | ea | 8
10.2.11 |  | 250mm | ea | 2
10.3 | Vol3 | SCADA System
Rate to include for the Supply only of the following Plant and Equipment Including Delivery, Storage, Quality Assurance and all Necessary Insurances
10.3.1 |  | PC Amount for SCADA Software | Prov. Sum | 1 | 950000 | 950000
10.3.2 |  | % Makup on SCADA Software | % | 950000
10.3.3 |  | PC Amount for SCADA Programing | Prov. Sum | 1 | 555000 | 555000
10.3.4 |  | % Makup on SCADA Programing | % | 555000
10.4 |  | ELECTRICAL DISTRIBUTION SYSTEM
Rate to include for the Supply only of the following Plant and Equipment Including Delivery, Storage, Quality Assurance and all Necessary Insurances
10.4.1 | PSX 2 | Level sensor and kiosk at Carlswarld Reservoir | No. | 1
10.4.2 | PSX 3 | Flow meter installation and kiosk at Reservoir Inlet | Sum | 1
10.4.3 | PSX 3 | Flow meter installation and kiosk at Reservoir Outlet | Sum | 1
10.4.4 |  | Notices at all Buildings | Sum | 1
10.4.5 | PSY 6 | Lightning protection of Carlswarld Reservoir | Sum | 1
10.4.6 | PSX 8.1 | Main Distrubution Board in Valve Building | Sum | 1
10.5 |  | Rate to include only for Handling including Double Handling if Stored, Transportation and Handling on site, Erection, Quality Assurance and Installation of The Following Plant and Equipment
10.5.1 | PSX 2 | Level sensor and kiosk at New Carlswarld Reservoir | No. | 1
10.5.2 | PSX 3 | Flow meter installation and kiosk at Reservoir Inlet | Sum | 1
10.5.3 | PSX 3 | Flow meter installation and kiosk at Reservoir Outlet | Sum | 1
10.5.4 |  | Notices at all Buildings | Sum | 1
10.5.5 | PSY 6 | Lightning protection of New Carlswarld Reservoir | Sum | 1
10.5.6 | PSX 8.1 | Main Distrubution Board in Valve Building | Sum | 1
SUB-TOTAL CARRIED FORWARD
brought forward
10.6 |  | Rate to include only for Installation, Commissioning, Testing And Adjusting The Following Plant and Equipment as a Completely Separate Operation Sometime after the Completion and/or Erection and Installation, Including Transportation And Accommodation for Personnel
10.6.2 | PSX 3 | Flow meter installation and kiosk at Reservoir Inlet | Sum | 1
10.6.3 | PSX 3 | Flow meter installation and kiosk at Reservoir Outlet | Sum | 1
10.6.4 |  | Notices at all Buildings | Sum | 1
10.6.5 | PSY 6 | Lightning protection of New Carlswarld Reservoir | Sum | 1
10.6.6 | PSX 8.1 | Main Distrubution Board in Valve Building | Sum | 1
ELECTRICAL INSTALLATION IN BUILDINGS AND ON STRUCTURES
10.7 |  | Rate to include for the Supply only of the following Plant and Equipment Including Delivery, Storage, Quality Assurance and all Necessary Insurance
10.7.1 | PSY 8.2 | Complete electrical installation in new Carswarld valve buiding DB-01 | Sum | 1
10.7.2 | DRW's | Type A Light Fitting | No. | 3
10.7.3 | DRW's | Type B Light Fitting | No. | 3
10.7.4 | DRW's | Type C Light Fitting | No. | 4
10.7.5 | PSY 4.2 | Area Lighting Fitting | No. | 8
10.7.6 | PSY 4.3 | Aviation Light Fitting on the Reservoir | No. | 4
10.7.7 | PSY 8.3 | Area Light Fitting on the Reservoir | No. | 6
10.7.8 | PSY 8.3 | Complete electrical installation in new Carswarld ReservoirReservoir Telemetry Hut DB-02 | Sum | 1
10.7.9 | DRW's | Type A Light Fitting | No. | 1
10.7.10 | PSY 4 | Area Lighting Fitting | No. | 4
10.7.11 | PSY 8.3 | Complete electrical installation in new Carswarld Reservoir Guard Hut DB-03 | Sum | 1
10.7.12 | DRW's | Type A Light Fitting | No. | 1
10.7.13 | DRW's | Type B Light Fitting | No. | 1
10.7.14 | PSY 4 | Area Lighting Fitting | No. | 4
| PSY 4 | Lighting installation on Carswarld Reservoir Site
10.7.15 | PSY 4.1 | 15m Highmast pole with 3X208W LED type Flood lights for area lighting | No. | 2
10.8 |  | Rate to include only for Handling including Double Handling if Stored, Transportation and Handling on site, Erection, Quality Assurance and Installation of The Following Plant and Equipment
10.8.1 | PSY 8.2 | Complete electrical installation in new Carswarld valve buiding DB-01 | Sum | 1
10.8.2 | DRW's | Type A Light Fitting | No. | 3
10.8.3 | DRW's | Type B Light Fitting | No. | 3
10.8.4 | DRW's | Type C Light Fitting | No. | 4
SUB-TOTAL CARRIED FORWARD
brought forward
10.8.5 | PSY 4.2 | Area Lighting Fitting | No. | 8
10.8.6 | PSY 4.3 | Aviation Light Fitting on the Reservoir | No. | 4
10.8.7 | PSY 8.3 | Area Light Fitting on the Reservoir | No. | 6
10.8.8 | PSY 8.3 | Complete electrical installation in new Carswarld ReservoirReservoir Telemetry Hut DB-02 | Sum | 1
10.8.9 | DRW's | Type A Light Fitting | No. | 1
10.8.10 | PSY 4 | Area Lighting Fitting | No. | 4
10.8.11 | PSY 8.3 | Complete electrical installation in new Carswarld Reservoir Guard Hut DB-03 | Sum | 1
10.8.12 | DRW's | Type A Light Fitting | No. | 1
10.8.13 | DRW's | Type B Light Fitting | No. | 1
10.8.14 | PSY 4 | Area Lighting Fitting | No. | 4
| PSY 4 | Lighting installation on Carswarld Reservoir Site
10.8.15 | PSY 4.1 | 15m Highmast pole with 3X208W LED type Flood lights for area lighting | No. | 2
10.9 |  | Rate to include only for Installation, Commissioning, Testing And Adjusting The Following Plant and Equipment as a Completely Separate Operation Sometime after the Completion and/or Erection and Installation, Including Transportation And Accommodation for Personnel
10.9.1 | PSY 8.2 | Complete electrical installation in new Carswarld valve buiding DB-01 | Sum | 1
10.9.2 | DRW's | Type A Light Fitting | No. | 3
10.9.3 | DRW's | Type B Light Fitting | No. | 3
10.9.4 | DRW's | Type C Light Fitting | No. | 4
10.9.5 | PSY 4.2 | Area Lighting Fitting | No. | 8
10.9.6 | PSY 4.3 | Aviation Light Fitting on the Reservoir | No. | 4
10.9.7 | PSY 8.3 | Area Light Fitting on the Reservoir | No. | 6
10.9.8 | PSY 8.3 | Complete electrical installation in new Carswarld ReservoirReservoir Telemetry Hut DB-02 | Sum | 1
10.9.9 | DRW's | Type A Light Fitting | No. | 1
10.9.10 | PSY 4 | Area Lighting Fitting | No. | 4
10.9.11 | PSY 8.3 | Complete electrical installation in new Carswarld Reservoir Guard Hut DB-03 | Sum | 1
10.9.12 | DRW's | Type A Light Fitting | No. | 1
10.9.13 | DRW's | Type B Light Fitting | No. | 1
10.9.14 | PSY 4 | Area Lighting Fitting | No. | 4
| PSY 4 | Lighting installation on Carswarld Reservior Site
10.9.15 | PSY 4.1 | 15m Highmast pole with 3X208W LED type Flood lights for area lighting | No. | 2
SUB-TOTAL CARRIED FORWARD
brought forward
| PSX 5 | TELEMETRY SYSTEM
10.10 |  | Rate to include for the Supply only of the following Plant And Equipment Including Delivery, Storage, Quality Assurance and all Necessary Insurances
10.10.1 |  | Changes to existing SCADA system at JW Control Room to add I/O for the new site as per new telemetry system below | Sum | 1
10.10.2 |  | New telemetry system at Carlswarld Reservoir | Sum | 1
10.11 |  | Rate to include only for Handling including Double Handling if Stored, Transportation and Handling on site, Erection, Quality Assurance and Installation of The Following Plant and Equipment
10.11.1 |  | Changes to existing SCADA system at JW Control Room to add I/O for the new site as per new telemetry system below | Sum | 1
10.11.2 |  | New telemetry system at Carlswarld Reservoir | Sum | 1
10.12 |  | Rate to include only for Installation, Commissioning, Testing and Adjusting the following Plant and Equipment as a Completely Separate Operation Sometime after the Completion and/or Erection and Installation, Including Transportation and Accommodation for personnel
10.12.1 |  | Changes to existing SCADA system at JW Control Room to add I/O for the new site as per new telemetry system below | Sum | 1
10.12.2 |  | New telemetry system at Carlswarld Reservoir | Sum | 1
MULTICORE CABLES AND EARTHWIRES
10.13 | PSY 1.7 & PSY 1.9 | Rate to include for the Supply only of the following Plant and Equipment Including Delivery, Storage, Quality Assurance and all Necessary Insurance
10.13.1 | a | 2.5mm² 3 - Core Cable | m | 280
10.13.2 | b | 70mm² Bare Copper Earth Wire | m | 300
10.13.3 | c | 16mm² 3 - Core Cable | m | 655
10.13.4 | d | 16mm² Bare Copper Cable | m | 265
10.13.5 | e | 16mm² 4-Core Cable | m | 75
10.13.6 | E06.4.17 | Cable route markers | No. | 12
10.13.7 | E06.4.1 | Concrete cable slabs (200 x 400 x 40) | No. | 220
10.13.8 | E06.9 | Cable name tags | Sum | 1
10.13.9 | E06.3.6 | Cable supports | Sum | 1
10.13.10 |  | Pump set sensor termination cubicle | No. | 1
10.13.11 |  | Core drilling 100mm diameter holes through 250mm concrete | No. | 5
10.14 | PSY 1.7 | Rate to include only for Installation, Commissioning, Testing and Adjusting the following Plant and Equipment as a Completely Separate Operation Sometime after the Completion and/or Erection and Installation, Including Transportation and Accommodation for personnel
10.14.1 | a | 2.5mm² 3 - Core Cable | m | 280
10.14.2 | b | 70mm² Bare Copper Earth Wire | m | 300
10.14.3 | c | 16mm² 3 - Core Cable | m | 655
10.14.4 | d | 16mm² Bare Copper Cable | m | 265
10.14.5 | e | 16mm² 4-Core Cable | m | 75
SUB-TOTAL CARRIED FORWARD
brought forward
| E16 | POWER SUPPLY UNITS
10.15 |  | The tendered rate shall include full compensation for the manufacture, supply, testing and delivery of the UPS incorporating all options/extras as detailed in the detail specification.
10.15.1 | E16.10 | Supply and deliver UPS | No. | 2
10.15.2 | E16.10 | Supply and deliver 1kVA hybrid inverter with 4x100Ah batteries for Aviation lights. | No. | 2
10.16 |  | The tendered rate shall include full compensation for the installation, site testing and commissioning plus the 12 months maintenance of the UPS incorporating all options/extras as detailed in the detail specification.
10.16.1 | E16.10 | Install standby UPS | No. | 2
10.16.2 | E16.10 | Supply and deliver 1kVA hybrid inverter with 4x100Ah batteries for Aviation lights | No. | 2
10.17 |  | The tendered rate shall include full compensation for the manufacture, supply, testing and delivery of the support platform/stand for UPS as detailed in the detail specification.
10.17.1 | E16.10 | Supply and deliver support platform/stand for UPS | No. | 2
10.17.2 | E16.10 | Supply and deliver 1kVA hybrid inverter with 4x100Ah batteries for Aviation lights | No. | 2
10.18 |  | The tendered rate shall include full compensation for the installation of the support platform/stand as detailed in the detail specification.
10.18.1 | E16.10 | Install support platform/stand for UPS | No. | 2
10.18.2 | E16.10 | Supply and deliver 1kVA hybrid inverter with 4x100Ah batteries for Aviation lights | No. | 2
10.19 |  | ACCESS CONTROL AND CCTV SYSTEM
Rate to include for the Supply only of the following Plant and Equipment Including Delivery, Storage, Quality Assurance and all Necessary Insurance
10.19.1 |  | PC Amount for Access control system | Prov. Sum | - | 350000 | 350000
10.19.2 |  | % Makup on Acces control system | % | 350000
10.19.3 |  | PC Amount for CCTV system | Prov. Sum | 1 | 2000000 | 2000000
10.19.4 |  | % Markup on CCTV System | % | 2000000
BULK ELECTRICAL CONNECTION
10.20 |  | Rate to include the supply of the following Plant and Equipment including Delivery, Storage, Quality Assurance and all necessary insurance.
10.20.1 |  | PC Amount for 60A 3 Phase Connection from Eskom | Prov. Sum | 1 | 55000 | 55000
10.20.2 |  | % Makup on 3Phase connection from Eskom | % | 55000
10.20.3 |  | PC Amount for Infrustructure to get Bulk Connection | Prov. Sum | 1 | 75000 | 75000
10.20.4 |  | % Makup on Item above | % | 75000
EARTHING AND LIGHTING PROTECTION
10.21 | PSY1.6 | Rate to include the supply of the following Plant and Equipment including Delivery, Storage, Quality Assurance and all necessary insurance.
10.21.1 | E11.17 | Earth resistivity tests | No | 1
SUB-TOTAL CARRIED FORWARD
brought forward
10.21.2 | E11.17 | Design of a Lightning Protection System (LPS) .. | No | 1
10.21.3 | PSY 1.6 | Installation of a structure LPS | Sum | 1
10.21.4 | E11.17 | Extra over for the supply and installation of additional 6m rod type earth electrodes including welding/clamps for the connection of earth-termination conductors | No | 20
10.21.5 | E11.17 | Provision for additional earthing as required | Prov. Sum | 1 | 35000 | 35000
10.21.6 | E11.17 | Testing of a LPS. | Sum | 1
10.22 |  | STANDBY GENERATOR
10.22.1 |  | The complete supply, delivery, installation, testing and commissioning of a 15kVA, 380V, standby emergency generator including fuel tank, weather proof & sound proof enclosure | Sum | 1
10.22.2 |  | All necessary electical cabling, DB, etc between standby generator and power supply of Reservoir facility | Sum | 1
TOTAL FOR SECTION 10 (Carried to Summary)

## Summary
SUMMARY OF BoQ
SUMMARY OF BILL OF QUANTITIES
Section | Description |  | Amount (R)
1 | Preliminary and General |  |  | don’t go lower than 15% | #DIV/0! | 7143000
2 | Site Preparation and Fencing
3 | Roads & Stormwater
4 | Reservoir
5 | Chambers & Boxes
6 | Interconnecting Pipework
7 | Guard House
8 | Telemetry Building
9 | Valve Building
10 | Electrical and C&I |  |  |  |  | 0 | #REF!
| Sub-Total 1 |  | 0 | 62.3<>
The above prices are Not Firm.
In respect of the total value of work done by approved SMME's at 30% of Sub Total 1 (This total shall include all amounts payable to SMME's, including P&G's)
= R.........................…................................................................ (A)
PSA 8.10.1 | Allowance as a percentage (maximum 15%) for appointing and handling work done by approved SMME's…...................................................................................% (B)
Sub Total 2 [Handling fees for sub contracting = (A) x (B)]
| Sub Total 3 = Sub Total 1 + Sub Total 2 |  | 0
ADD | 10% Contingency |  | 0
Sub-Total 4
ADD | VAT @ 15% |  | 0
TOTAL CARRIED TO FORM OFFER

## Sheet1 (hidden)
4400 | 6241.4841 | 5674.0764 |  | 37448.9046 | 36000
|  | 34044.4587 |  | 374.489 | 711529.1867
46800 |  | 7.128 | 85.536
48000