## Cover
Johannesburg Water (SOC) Ltd
JW14358
Construction of Woodmead Inlet Bulk
Water Pipeline
Schedule of Quantities
`

## P&G
Part A - Section 1: Preliminary and general
General
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 A | 1 | GENERAL
8.3 | 1.01 | Scheduled fixed-charge and value-related items:
PSA 8.3.1 | 1.01.01 | Contractual Requirements |  |  | 0
| 1.01.01.01 | Loss of or damage to the works, Plant and Material | sum | 1
| 1.01.01.02 | Loss of or damage to Equipment | sum | 1
| 1.01.01.03 | Loss of or damage to property (except the works, Plant, | sum | 1
Materials and Equipment) and liability for bodily injury
to or death of a person (not an employee of the
Contractor) arising from or in connection with the
Contractor Providing the Works for any one event
| 1.01.01.04 | Death of or bodily injury to employees of the Contractor | sum | 1
arising out of and in the course of their employment in
connection with the contract for any one event
PSA 8.3.2 | 1.01.02 | Establishment of Facilities on the Site
PSA 8.3.2.1 | 1.01.02.01 | Facilities for Engineer
| 1.01.02.01.01 | a) Furnished offices (2 No.) | sum | 1
| 1.01.02.01.02 | c) Name Boards (4 No.) | sum | 1
| 1.01.02.01.03 | d) JW ISD team office (2 No.) | sum | 1
| 1.01.02.01.04 | e) CLO's office (1 No.) | sum | 1
| 1.01.02.01.05 | f) Meeting Room (1 No.) | sum | 1
| 1.01.02.01.06 | g) Latrine Facilities (1 No.) | sum | 1
| 1.01.02.01.07 | h) Parking (3 No.) | sum | 1
| 1.01.02.01.08 | i) Communication | sum | 1
| 1.01.02.01.09 | j) Survey equipment, assistants and material | sum | 1
| 1.01.02.01.10 | k) Computer facilities | sum | 1
PSA 8.3.2.2 | 1.01.02.02 | Facilities for Contractor
| 1.01.02.02.01 | a) Offices and storage sheds | sum | 1
| 1.01.02.02.02 | b) Workshops | sum | 1
| 1.01.02.02.03 | e) Ablution and latrine facilities | sum | 1
| 1.01.02.02.04 | f) Tools and equipment | sum | 1
| 1.01.02.02.05 | g) Water supplies, electric power and communications | sum | 1
| 1.01.02.02.06 | h) Dealing with water (See 5.5) | sum | 1
Carried forward
Part A - Section 1: Preliminary and general
General
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 1.01.02.02.07 | i) Access (See 5.8) | sum | 1
| 1.01.02.02.08 | j) Plant | sum | 1
PSA 8.3.3 | 1.01.03 | Other Fixed charge Obligations | sum | 1
8.3.4 | 1.01.04 | Removal of Site Establishment | sum | 1
PSA 8.3.5 | 1.01.05 | Additional Contractual Obligations
PSA 8.3.5.1 | 1.01.05.01 | Notice and warning to consumers | sum | 1
PSA 8.3.5.2 | 1.01.05.02 | Compile Health and Safety Plan | sum | 1
PSA 8.3.5.3 | 1.01.05.03 | EMP Obligations | sum | 1
PSA 8.3.5.4 | 1.01.05.04 | Provision of Photographic Records | sum | 1
8.4 | 1.02 | Scheduled time-related items:
PSA 8.4.1 | 1.02.01 | Contractual Requirements | sum | 1
| 1.02.01.01 | Loss of or damage to the works, Plant and Material | sum | 1
| 1.02.01.02 | Loss of or damage to Equipment | sum | 1
| 1.02.01.03 | Loss of or damage to property (except the works, Plant, | sum | 1
Materials and Equipment) and liability for bodily injury
to or death of a person (not an employee of the
Contractor) arising from or in connection with the
Contractor Providing the Works for any one event
| 1.02.01.04 | Death of or bodily injury to employees of the Contractor | sum | 1
arising out of and in the course of their employment in
connection with the contract for any one event
PSA 8.4.2 | 1.02.02 | Operation and Maintenance of Facilities on Site, for
Duration of Construction, except where otherwise
stated
PSA 8.4.2.1 | 1.02.02.01 | Facilities for Engineers
| 1.02.02.01.01 | a) Furnished offices (2 No.) | sum | 1
| 1.02.02.01.02 | c) Name Boards (2 No.) | sum | 1
| 1.02.02.01.03 | d) Survey assistants and materials | sum | 1
| 1.02.02.01.04 | e) JW ISD team office (2 No.) | sum | 1
| 1.02.02.01.05 | f) CLO's office (1 No.) | sum | 1
| 1.02.02.01.06 | g) Meeting Room (1 No.) | sum | 1
| 1.02.02.01.07 | h) Latrine Facilities (1 No.) | sum | 1
| 1.02.02.01.08 | i) Parking (3 No.) | sum | 1
Carried forward
Part A - Section 1: Preliminary and general
General
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
| Brought forward |  |  |  |  | 0
| 1.02.02.01.09 | j) Communication | sum | 1
| 1.02.02.01.10 | k) Computer facilities | sum | 1
PSA 8.4.2.2 | 1.02.02.02 | Facilities for Contractor
| 1.02.02.02.01 | a) Offices and storage sheds | sum | 1
| 1.02.02.02.02 | b) Workshops | sum | 1
| 1.02.02.02.03 | e) Ablution and latrine facilities | sum | 1
| 1.02.02.02.04 | f) Tools and equipment | sum | 1
| 1.02.02.02.05 | g) Water supplies, electric power and communications | sum | 1
| 1.02.02.02.06 | h) Dealing with water (See 5.5) | sum | 1
| 1.02.02.02.07 | i) Access to site (See 5.8) | sum | 1
| 1.02.02.02.08 | j) Plant | sum | 1
PSA 8.4.3 | 1.02.03 | Supervision for duration of construction | sum | 1
PSA 8.4.4 | 1.02.04 | Company and head office overhead costs for duration of the Contract | sum | 1
PSA 8.4.5 | 1.02.05 | Other time-related obligations | sum | 1
PSA 8.4.6 | 1.02.06 | Additional Obligations
PSA 8.4.6.1 | 1.02.06.01 | Implementation of Health and Safety Plan | sum | 1
PSA 8.4.6.2 | 1.02.06.02 | Full-time OHS Officer | sum | 1
PSA 8.4.6.3 | 1.02.06.03 | Provide protective safety clothing | sum | 1
PSA 8.4.6.4 | 1.02.06.04 | EMP Obligations | sum | 1
PSA 8.4.6.5 | 1.02.06.05 | Full-time Environmental Representative | sum | 1
PSA 8.4.6.6 | 1.02.06.06 | On-site security | sum | 1
PSA 8.4.6.7 | 1.02.06.07 | On-site security at Office Park during electrical fence construction | sum | 1
PSA 8.4.6.8 | 1.02.06.08 | Electrical Safety Officer (ESO) | sum | 1
PSA 8.4.6.9 | 1.02.06.09 | Advertising on the Billboard | P. Sum | 1 | 360000 | 360000
| 1.02.06.09.01 | a) Overheads, charges and profit on above | %
PSA 8.4.6.10 | 1.02.06.10 | Temporary Removal and reinstatement of billboard | P. Sum | 1 | 920000 | 920000
Carried forward
Part A - Section 1: Preliminary and general
General
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
| Brought forward |  |  |  |  | 0
PSA 8.5 | 1.03.01 | a) Community Liaison Officer (CLO and CSO) | P. Sum | 1 | 400000 | 400000
| 1.03.02 | b) Overheads, charges and profit on above | % |  |  | 0
| 1.03.03 | c) Alteration to existing services by authorities | P. Sum | 1 | 1000000 | 1000000
| 1.03.04 | d) Overheads, charges and profit on above | % |  |  | 0
| 1.03.05 | e) Reinstatement of asphalt by JRA | P. Sum | 1 | 8000000 | 8000000
| 1.03.06 | f) Overheads, charges and profit on above | % |  |  | 0
| 1.03.07 | g) Training | P. Sum | 1 | 400000 | 400000
| 1.03.08 | h) Overheads, charges and profit on above | % |  |  | 0
| 1.03.09 | i) Temporary protection of services | P. Sum | 1 | 400000 | 400000
| 1.03.10 | j) Overheads, charges and profit on above | % |  |  | 0
| 1.03.11 | k) Relocation of endangered plant species | P. Sum | 1 | 150000 | 150000
| 1.03.12 | l) Overheads, charges and profit on above | % |  |  | 0
| 1.03.13 | m) Provision of OHS Mentorship | P. Sum | 1 | 80000 | 80000
| 1.03.14 | n) Overheads, charges and profit on above | % |  |  | 0
| 1.03.15 | o) Internships | P. Sum | 1 | 960000 | 960000
| 1.03.16 | p) Overheads, charges and profit on above | % |  |  | 0
| 1.03.17 | q) Social Consultant | P. Sum | 1 | 600000 | 600000
| 1.03.18 | r) Overheads, charges and profit on above | % |  |  | 0
| 1.03.19 | s) 10% Preliminary and General Items for SMMEs | P. Sum | 1 | 5500000 | 5500000
PSA 8.6 | 1.04 | Prime Cost Items: |  |  |  | 0
| 1.04.01 | a) Additional tests required by the Project Manager | PC Sum | 1 | 200000 | 200000
| 1.04.02 | b) Charge required by Contractor on subitem 1.04.01 above | %
PSA 8.7 | 1.05 | Dayworks
| 1.05.01 | Labour
| 1.05.01.01 | Foreman | h | 40
| 1.05.01.02 | Welder | h | 40
| 1.05.01.03 | Skilled labour | h | 80
| 1.05.01.04 | Semi-skilled labour | h | 80
| 1.05.01.05 | Unskilled labour | h | 160
Carried forward
Part A - Section 1: Preliminary and general
General
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 1.05.02 | Plant
| 1.05.02.01 | Excavator (20 t) | h | 40
| 1.05.02.02 | Excavator (30 t) | h | 40
| 1.05.02.03 | Loader (0,5 m³ bucket) | h | 40
| 1.05.02.04 | Tipper truck (10 m3) | h | 40
| 1.05.02.05 | Walk-behind vibrating roller | h | 40
| 1.05.02.06 | Welding Machine | h | 40
| 1.05.02.07 | Water truck (5 000ℓ) | h | 40
| 1.05.02.08 | Water pump (4 inch) | h | 40
PSA 8.8 | 1.06 | Temporary works (See 8.1.2.1(d))
PSA 8.8.4 | 1.06.01 | Existing services (see 5.4)
| 1.06.01.01 | a) Supply or hire of Ground Penetrating Radar equipment | Sum | 1
| 1.06.01.02 | b) Excavation by hand to expose existing services in all types of materials | m³ | 1500
PSA 8.8.7 | 1.06.02 | Temporary Plastic Barrier Fence | m | 6600
Carried forward to summary (Part A - Section 1)
Part A - Section 1: Preliminary and general
General
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SUMMARY
SANS 1200 A |  | GENERAL
Total carried forward to summary

## DN 600 MAIN
Part B - Section 1: DN 600 Steel Main Pipeline
Site clearance
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 C | 1 | SITE CLEARANCE
Refer to Drawing:
JW14358-16941-T-012-S01-00-TMS
PSC 8.2.1 | 1.01 | Clear and grub
| 1.01.01 | Strips, 3 m wide | m | 4200
8.2.2 | 1.02 | Remove and grub large trees and tree stumps of girth
| 1.02.01 | Over 1 m and up to and including 2 m | No. | 9
| 1.02.02 | Over 2 m and up to and including 3 m | No. | 15
PSC 8.2.5 | 1.03 | Take down existing fences, guardrails and masonry
walls
| 1.03.01 | a) Guardrails | m | 800
| 1.03.02 | b) Diamond mesh fencing | m | 400
| 1.03.03 | c) Steel palisade fencing | m | 800
| 1.03.04 | d) Clearview fencing | m | 400
| 1.03.05 | e) 110 mm masonry wall | m | 100
| 1.03.06 | f) 220 mm masonry wall | m | 100
| 1.03.07 | g) Masonry columns | m³ | 100
8.2.10 | 1.04 | Remove topsoil to nominal depth of 150 mm and | m³ | 1890
stockpile
PSC 8.2.11 | 1.05 | Temporary fencing or hoarding
| 1.05.01 | a) 1.8 m High Diamond mesh fencing | m | 1000
PSC 8.2.12 | 1.06 | Removal of man-made surfaces and kerbing
| 1.06.01 | a) Road materials with Asphalt ≤ 50mm thick | m² | 325
| 1.06.02 | b) Road materials with Asphalt > 50 ≤ 100mm thick | m² | 1125
| 1.06.03 | c) Interlocking concrete segmental paving blocks, Class 2.6/40MPa (all colours) | m² | 3820
| 1.06.04 | d) Concrete paving blocks, Class 2.6/40MPa (various sizes) | m² | 500
| 1.06.05 | e) Brick paving | m² | 100
| 1.06.06 | f) Unreinforced concrete ≤ 75mm thick | m² | 100
| 1.06.07 | g) Reinforced concrete ≤ 75mm thick | m² | 250
| 1.06.08 | h) Garden, lawns and grassing | m² | 2550
| 1.06.09 | i) All types of Kerbing including channel | m | 2550
Carried forward
Part B - Section 1: DN 600 Steel Main Pipeline
Site clearance
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSC 8.2.13 | 1.07 | Backfilling and reinstatement of man-made surfaces re-using removed materials
| 1.07.01 | a) Interlocking concrete segmental paving blocks, | m² | 2000
Class 2.6/40MPa (all colours)
| 1.07.02 | b) Concrete paving blocks, Class 2.6/40MPa | m² | 500
(various sizes)
| 1.07.03 | c) Brick paving | m² | 100
| 1.07.04 | d) Kerbing (all types of kerbing) | m | 1500
PSC 8.2.14 | 1.08 | Take down and re-erect existing fences and
guardrails
| 1.08.01 | a) Guardrails | m | 1200
| 1.08.02 | b) Diamond mesh fencing | m | 800
| 1.08.03 | c) Steel palisade fencing | m | 800
| 1.08.04 | d) Clearview fencing | m | 400
PSC 8.2.15 | 1.09 | Reinstatement of existing masonry walls, steel
fences and guard rails using new materials
PSC 8.2.15.1 | 1.09.1 | Face brick walls
| 1.09.1.1 | a) 110 mm wall | m² | 150
| 1.09.1.2 | b) 220 mm wall | m² | 150
| 1.09.1.3 | c) Masonry columns | m³ | 100
PSC 8.2.15.2 | 1.09.2 | Plastered walls
| 1.09.2.01 | a) 110 mm wall | m² | 150
| 1.09.2.02 | b) 220 mm wall | m² | 150
| 1.09.2.03 | c) Masonry columns | m³ | 100
PSC 8.2.15.3 | 1.09.3 | Steel fences
| 1.09.3.01 | a) Diamond mesh fencing | m² | 200
| 1.09.3.02 | b) Palisade fencing | m² | 1800
| 1.09.3.03 | c) Clearview fencing | m² | 150
PSC 8.2.16 | 1.10 | Protection of trees | No | 20
Carried forward
Part B - Section 1: DN 600 Steel Main Pipeline
Site clearance
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSC 8.2.21 | 1.11 | Temporary removal and reinstatement of electrical
infrastructure
| 1.11.01 | a) Electrical Poles | No | 20
| 1.11.02 | b) Street Lights | No | 20
| 1.11.03 | c) Traffic Signals | No | 40
PSC 8.2.22 | 1.12 | Temporary removal and reinstatement of electrical
fencing
| 1.12.01 | a) Wall top mounted | m | 175
| 1.12.02 | b) Free standing (fence height up to 3 meter) | m | 500
| 1.12.03 | c) Add-On Fence attached to palisade fence | m | 500
(fence height up to 3 meter)
PSC 8.2.23 | 1.13 | Temporary electrical fencing
| 1.13.01 | a) Wall top mounted | m | 500
| 1.13.02 | b) Free standing (fence height up to 3 meter) | m | 500
PSC 8.2.24 | 1.14 | Construction of dry stack precast block retaining | m² | 60
wall
Carried forward to summary (Part B - Section 1)
Part B - Section 1: DN 600 Steel Main Pipeline
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 DB | 2 | EARTHWORKS (PIPE TRENCHES)
Refer to Drawing:
JW14358-16941-T-012-S01-00-TMS
PSDB 8.3.2 | 2.01 | a) Excavate in all materials, for trenches, backfill compact and dispose of surplus material
| 2.01.01 | Pipes of diameter of DN 600 for depths
| 2.01.01.01 | Up to 1,0 m | m | 100
| 2.01.01.02 | Over 1,0 m up to 2,0 m | m | 2500
| 2.01.01.03 | Over 2,0 m up to 3,0 m | m | 2500
| 2.01.01.04 | Over 3,0 m up to 4,0 m | m | 380
PSDB 8.3.2 | 2.02 | b) Extra over item 2.01 above for
| 2.02.01 | 1) Intermediate excavation | m³ | 2250
| 2.02.02 | 2) Hard rock excavation | m³ | 2250
| 2.02.03 | 3) Hand excavation where ordered by the Project Manager
| 2.02.03.01 | a) Soft material | m³ | 700
| 2.02.03.02 | b) Intermediate material | m³ | 700
| 2.02.03.03 | c) Hard material | m³ | 200
PSDB 8.3.2 | 2.02.04 | 4) Backfill stabilized with 5% cement where directed by the Project Manager | m³ | 700
PSDB 8.3.2 | 2.02.05 | 5) Soilcrete backfill where directed by the Project Manager | m³ | 700
8.3.2 | 2.02.06 | c) Excavate and dispose of unsuitable material from trench bottom (provisional) | m³ | 800
8.3.3 | 2.03 | Excavation Ancillaries
8.3.3.1 | 2.03.01 | Make up deficiency in backfill material
| 2.03.01.01 | a) from other necessary excavations on site | m³ | 600
| 2.03.01.02 | c) by importation from commercial or off-site sources selected by the contractor | m³ | 600
PSDB 8.3.3.3 | 2.03.02 | Compaction in roadways | m³ | 850
PSDB 8.3.4 | 2.04 | Particular Items
PSDB 8.3.4 (a) | 2.04.01 | a) Shore trench opposite structure or service | m | 1000
PSDB 8.3.4 (c) | 2.04.02 | Dealing with groundwater
| 2.04.02.01 | (1) Crushed stone (14 mm or 20 mm) | m³ | 400
| 2.04.02.02 | (2) Nonwoven, needle punched, continuous filament, polyester Geotextile | m2 | 3600
Carried forward
Part B - Section 1: DN 600 Steel Main Pipeline
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSDB 8.3.5 | 2.05 | Existing Services that Intersect or Adjoin a Pipe Trench
PSDB 8.3.5 | 2.05.01 | a) Services that intersect a trench
| 2.05.01.01 | Water pipes up to DN 200 | No. | 20
| 2.05.01.02 | Water mains DN 250 and larger | No. | 10
| 2.05.01.03 | Sewer pipes up to DN 160 | No. | 20
| 2.05.01.04 | Sewer mains DN 200 and larger | No. | 10
| 2.05.01.05 | Stormwater pipes (any size) | No. | 40
| 2.05.01.06 | Cables (Electrical, data or telephone) | No. | 50
| 2.05.01.07 | Drainage furrows and channels | No. | 20
PSDB 8.3.5 | 2.05.02 | b) Services that adjoin a trench
| 2.05.02.01 | Water pipes up to DN 200 | m | 500
| 2.05.02.02 | Water mains DN 250 and larger | m | 200
| 2.05.02.03 | Sewer pipes up to DN 160 | m | 500
| 2.05.02.04 | Sewer mains DN 200 and larger | m | 200
| 2.05.02.05 | Stormwater pipes (any size) | m | 1000
| 2.05.02.06 | Cables (Electrical, data or telephone) | m | 1000
| 2.05.02.07 | Drainage furrows and channels | m | 200
PSDB 8.3.5 c | 2.06.03 | c) Services that require special care
| 2.06.03.01 | Crossing underneath power lines up to 11 kV | No. | 2
| 2.06.03.02 | Crossing underneath power lines up to 300 kV | No. | 1
| 2.06.03.03 | Crossing underneath telephone lines | No. | 20
| 2.06.02.04 | Working alongside electricity poles | No. | 25
| 2.06.02.05 | Working alongside telephone poles | No. | 55
| 2.06.02.06 | Working alongside traffic signals | No. | 100
| 2.06.02.07 | Working alongside street lights | No. | 200
Carried forward
Part B - Section 1: DN 600 Steel Main Pipeline
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSDB 8.3.6 | 2.07 | Finishing
PSDB8.3.6.1 | 2.07.01 | Reinstate road surfaces complete with all courses
| 2.07.01.01 | a) Gravel on shoulders | m² | 126
| 2.07.01.02 | b) Asphalt of thickness 40 mm in parking area | m² | 210
| 2.07.01.03 | c) Asphalt of thickness 40 mm in roadway | m² | 420
| 2.07.01.04 | d) Re-instatement of unreinforced concrete | m² | 2050
| 2.07.01.05 | e) Re-instatement of reinforced concrete | m³ | 2050
| 2.07.01.06 | f) Re-instatement of bricks, concrete pre-cast units and interlocking concrete segmental paving | m² | 4100
| 2.07.01.07 | g) Re-instatement of grouted brick paving, complete | m² | 4100
| 2.07.01.08 | h) Re-instatement of gardens, lawns and grassing | m² | 3420
PSDB8.3.6.2 | 2.07.02 | Reinstatement of surfacing for walkways
| 2.07.02.01 | a) Re-instatement of walkways with unreinforced concrete | m² | 200
| 2.07.02.02 | b) Re-instatement of walkways with interlocking concrete segmental paving | m² | 1500
PSDB8.3.6.3 | 2.07.03 | Reinstatement of kerbs and channels
|  | a) Re-instatement of all types of precast kerbing, complete | m | 500
|  | b) Re-instatement of precast concrete gutter, complete | m | 300
|  | c) Re-instatement of all types of insitu cast concrete kerbing, complete | m | 100
|  | d) Re-instatement of all types of insitu cast concrete gutter, complete | m | 300
PSDB 8.3.7 | 2.08 | Accommodation of traffic | sum | 1
Carried forward to summary (Part B - Section 1)
Part B - Section 1: DN 600 Steel Main Pipeline
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 L | 3 | MEDIUM-PRESSURE PIPELINES
Refer to Drawing:
JW14358-16941-T-012-S01-00-TMS
PSL 8.2.16 | 3.01 | Supply, Lay and Bed Steel Pipes Complete with
Welded Joints
| 3.01.01 | DN 600 welded steel; 6 mm wall thickness; convex heat | m | 5000
sink steel ring joint; API 5L X42 steel pipe, with Rigid
Polyurethane Coating (RPU) and Solvent Free Liquid
Epoxy lining (SFE). Bedded and jointing as per
Drawing: JW14358-16941-T-017-S05-00-TMS
Drawing: JW14358-16941-T-017-S16-00-TMS
PSL 8.2.17 | 3.02 | Supply and install Steel Pipes inside Concrete Pipe
Jacking Sleeve Complete with Flanged Joints
| 3.02.01 | DN 600 flanged steel; 6 mm wall thickness; API 5L X42 | m | 110
steel pipe; with Rigid Polyurethane Coating (RPU) and
Solvent Free Liquid Epoxy lining (SFE); supplied in lengths
of exactly 6000 mm; both ends flanged to SANS 1123
Table 1600/3
PSL 8.2.18 | 3.03 | Supply and install Steel Pipes inside Concrete Pipe
Tunnel at M1 crossing Complete with Flanged Joints
| 3.03.01 | DN 600 flanged steel; 6 mm wall thickness; API 5L X42 | m | 84
steel pipe; with Rigid Polyurethane Coating (RPU) and
Solvent Free Liquid Epoxy lining (SFE); supplied in lengths
of exactly 6000 mm; both ends flanged to SANS 1123
Table 1600/3
PSL 8.2.19 | 3.04 | Extra over 3.01 for the Supplying, Laying, Welding or
Jointing and Bedding of Steel specials
| 3.04.01 | DN 600 steel; 6 mm wall thickness; API 5LX42 steel, long radius bends, with Rigid Polyurethane Coating (RPU)
long radius bends, with Rigid Polyurethane Coating (RPU)
and Solvent Free Liquid Epoxy lining (SFE):
| 3.04.01.01 | Item 1: DN 600, 46° up to 90°, 5 segment bend to | No. | 8
SANS 719; centre line radius R = 1220 mm, unflanged
| 3.04.01.02 | Item 2: DN 600, 23° up to 45°, 3 segment bend to | No. | 6
SANS 719; centre line radius R = 1220 mm, unflanged
| 3.04.01.03 | Item 3: DN 600, 11.25 up to 22.5°, 2 segment bend to | No. | 8
SANS 719; centre line radius R = 1220 mm, unflanged
| 3.04.01.04 | Item 4: DN 600, 90°, Flanged 5 segment bend to | No. | 1
SANS 719; centre line radius R = 1220 mm
| 3.04.02 | Mitres up to 11.25° | No. | 46
| 3.04.03 | DN 600 loose flanges to SANS 1123 table 1600/3 for | No. | 24
welding on site
Carried forward
Part B - Section 1: DN 600 Steel Main Pipeline
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSL 8.2.22 | 3.05 | Flushing and sterilising of pipelines
| 3.05.01 | DN 600 steel pipe | m | 5180
PSL 8.2.23 | 3.06 | Hydraulic field-testing of pipelines
| 3.06.01 | DN 600 steel pipe | m | 5180
PSL 8.2.24 | 3.07 | Pipeline and Valve Markers
| 3.07.01 | a) Precast Concrete Marker: | No. | 40
Drawing JW14358-16941-T-017-S07-00-TMS
| 3.07.02 | b) Kerb Marking | No. | 40
Drawing JW14358-16941-T-017-S07-00-TMS
PSL 8.2.35 | 3.08 | Extra-Over 8.3.16 for Forming Trial joint | Sum | 1
Carried forward to summary (Part B - Section 1)
Part B - Section 1: DN 600 Steel Main Pipeline
Bedding (pipes)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 LB | 4 | BEDDING (PIPES)
Refer to Drawing:
JW14358-16941-T-012-S01-00-TMS
PSLB 8.2.1.1 | 4.01 | Provision of bedding from trench excavations
without the need for screening or other treatments
| 4.01.01 | Selected granular material | m³ | 300
| 4.01.02 | Selected fill material | m³ | 600
PSLB 8.2.1.2 | 4.02 | Provision of bedding from trench excavations
including screening or other treatments
| 4.02.01 | Selected granular material | m³ | 600
| 4.02.02 | Selected fill material | m³ | 400
8.2.2 | 4.03 | Supply only of bedding by importation
| 4.03.01 | From other necessary excavations (Provisional)
| 4.03.01.01 | Selected granular material | m³ | 100
| 4.03.01.02 | Selected fill material | m³ | 100
| 4.03.02 | From commercial sources (Provisional)
| 4.03.02.01 | Selected granular material | m³ | 3700
| 4.03.02.02 | Selected fill material | m³ | 400
8.2.4 | 4.04 | Encasing of pipes in concrete
| 4.04.01 | Encasing DN 600 steel pipe
| 4.04.01.01 | Class 15 MPa/19 mm | m³ | 20
| 4.04.01.02 | Class 30 MPa/19 mm | m³ | 10
PSLB 8.2.6 | 4.05 | Extra over items 4.01 and 4.02 for bedding stabilized | m³ | 400
with 5% cement
PSLB 8.2.7 | 4.06 | Compaction Testing using a Nuclear Moisture Density | No. | 52
Gauge
Carried forward to summary (Part B - Section 1)
Part B - Section 1: DN 600 Steel Main Pipeline
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SUMMARY
SANS 1200 C |  | SITE CLEARANCE
SANS 1200 DB |  | EARTHWORKS (PIPE TRENCHES)
SANS 1200 L |  | MEDIUM-PRESSURE PIPELINES
SANS 1200 LB |  | BEDDING (PIPES)
Total carried forward to summary

## DN 600 BYPASS
Part B - Section 2: DN 600 Steel Bypass Pipeline
Site clearance
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 C | 1 | SITE CLEARANCE
Refer to Drawing:
JW14358-16941-T-012-S11-00-TMS
PSC 8.2.1 | 1.01 | Clear and Grub
| 1.01.01 | Strips, 3 m wide | m | 500
8.2.2 | 1.02 | Remove and grub large trees and tree stumps
of girth
| 1.02.01 | Over 1 m and up to and including 2 m | No. | 3
| 1.02.02 | Over 2 m and up to and including 3 m | No. | 5
PSC 8.2.5 | 1.03 | Take down existing fences, guardrails and
masonry walls
| 1.03.01 | a) Guardrails | m | 200
| 1.03.02 | b) Diamond mesh fencing | m | 50
| 1.03.03 | c) Steel palisade fencing | m | 30
| 1.03.04 | d) Clearview fencing | m | 50
| 1.03.05 | e) 110 mm masonry wall | m | 30
| 1.03.06 | f) 220 mm masonry wall | m | 30
8.2.10 | 1.04 | Remove topsoil to nominal depth of 150 mm and stockpile | m³ | 225
PSC 8.2.11 | 1.05 | Temporary fencing or hoarding
|  | a) 1.8 m High Diamond mesh fencing | m | 300
PSC 8.2.12 | 1.06 | Removal of man-made surfaces and kerbing
| 1.06.01 | a) Road materials with Asphalt ≤ 50mm thick | m² | 200
| 1.06.02 | b) Road materials with Asphalt > 50 ≤ 100mm thick | m² | 600
| 1.06.03 | c) Interlocking concrete segmental paving blocks, Class 2.6/40MPa (all colours) | m² | 100
| 1.06.04 | d) Concrete paving blocks, Class 2.6/40MPa (various sizes) | m² | 50
| 1.06.05 | e) Brick paving | m² | 50
| 1.06.06 | f) Unreinforced concrete ≤ 75mm thick | m² | 50
| 1.06.07 | g) Reinforced concrete ≤ 75mm thick | m² | 50
| 1.06.08 | h) Garden, lawns and grassing | m² | 50
| 1.06.09 | i) All types of Kerbing including channel | m | 300
Carried forward
Part B - Section 2: DN 600 Steel Bypass Pipeline
Site clearance
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSC 8.2.13 | 1.07 | Backfilling and reinstatement of man-made
surfaces re-using removed materials
| 1.07.01 | a) Interlocking concrete segmental paving blocks, | m² | 100
Class 2.6/40MPa (all colours)
| 1.07.02 | b) Concrete paving blocks, Class 2.6/40MPa (various | m² | 50
sizes)
| 1.07.03 | c) Brick paving | m² | 50
| 1.07.04 | d) Kerbing (all types of kerbing) | m | 200
PSC 8.2.14 | 1.08 | Take down and re-erect existing fences and
guardrails
| 1.08.01 | a) Guardrails | m | 160
| 1.08.02 | b) Diamond mesh fencing | m | 80
| 1.08.03 | c) Steel palisade fencing | m | 40
| 1.08.04 | d) Clearview fencing | m | 40
PSC 8.2.15 | 1.09 | Reinstatement of existing masonry walls, steel
fences and guard rails using new materials
PSC 8.2.15.1 | 1.09.1 | Face brick walls
| 1.09.1.1 | a) 110 mm wall | m² | 20
| 1.09.1.2 | b) 220 mm wall | m² | 20
PSC 8.2.15.2 | 1.09.2 | Plastered walls
| 1.09.2.01 | a) 110 mm wall | m² | 20
| 1.09.2.02 | b) 220 mm wall | m² | 20
PSC 8.2.15.3 | 1.09.3 | Steel fences
| 1.09.3.01 | a) Palisade fencing | m² | 20
| 1.09.3.02 | b) Clearview fencing | m² | 20
PSC 8.2.16 | 1.10 | Protection of trees | No | 6
PSC 8.2.21 | 1.11 | Temporary removal and reinstatement of
electrical infrastructure
| 1.11.01 | a) Electrical Poles | No | 6
| 1.11.02 | b) Street Lights | No | 6
| 1.11.03 | c) Traffic Signals | No | 5
Carried forward to summary (Part B - Section 2)
Part B - Section 2: DN 600 Steel Bypass Pipeline
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 DB | 2 | EARTHWORKS (PIPE TRENCHES)
Refer to Drawing:
JW14358-16941-T-012-S11-00-TMS
PSDB 8.3.2 | 2.01 | a) Excavate in all materials, for trenches, backfill
compact and dispose of surplus material
| 2.01.01 | Pipes of diameter of DN 600 for depths:
| 2.01.01.01 | Up to 1,0 m | m | 30
| 2.01.01.02 | Over 1,0 m up to 2,0 m | m | 50
| 2.01.01.03 | Over 2,0 m up to 3,0 m | m | 360
| 2.01.01.04 | Over 3,0 m up to 4,0 m | m | 150
PSDB 8.3.2 | 2.02 | Extra over item 2.01 above for:
| 2.02.01 | 1) Intermediate excavation | m³ | 180
| 2.02.02 | 2) Hard rock excavation | m³ | 180
| 2.02.03 | 3) Hand excavation where ordered by the Project Manager
| 2.02.03.01 | a) Soft material | m³ | 180
| 2.02.03.02 | b) Intermediate material | m³ | 180
| 2.02.03.03 | c) Hard material | m³ | 90
PSDB 8.3.2 | 2.02.04 | 4) Backfill stabilized with 5% cement where directed by | m³ | 350
the Project Manager
PSDB 8.3.2 | 2.02.05 | 5) Soilcrete backfill where directed by the Project Manager | m³ | 350
8.3.2 | 2.02.06 | c) Excavate and dispose of unsuitable material from | m³ | 100
trench bottom (provisional)
8.3.3 | 2.03 | Excavation Ancillaries
8.3.3.1 | 2.03.01 | Make up deficiency in backfill material
| 2.03.01.01 | a) from other necessary excavations on site | m³ | 80
| 2.03.01.02 | c) by importation from commercial or off-site sources selected by the contractor | m³ | 80
PSDB 8.3.3.3 | 2.03.02 | Compaction in roadways | m³ | 1200
PSDB 8.3.4 | 2.04 | Particular Items
PSDB 8.3.4 (a) | 2.02.04 | a) Shore trench opposite structure or service | m | 300
PSDB 8.3.4 (c) | 2.04.02 | Dealing with groundwater
| 2.04.02.01 | (1) Crushed stone (14 mm or 20 mm) | m³ | 40
| 2.04.02.02 | (2) Nonwoven, needle punched, continuous filament, polyester Geotextile | m2 | 360
Carried forward
Part B - Section 2: DN 600 Steel Bypass Pipeline
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSDB 8.3.5 | 2.05 | Existing Services that Intersect or Adjoin a Pipe Trench
PSDB 8.3.5 | 2.05.01 | a) Services that intersect a trench
| 2.05.01.01 | Water pipes up to DN 200 | No. | 5
| 2.05.01.02 | Water mains DN 250 and larger | No. | 3
| 2.05.01.03 | Sewer pipes up to DN 160 | No. | 5
| 2.05.01.04 | Sewer mains DN 200 and larger | No. | 3
| 2.05.01.05 | Stormwater pipes (any size) | No. | 10
| 2.05.01.06 | Cables (Electrical, data or telephone) | No. | 20
| 2.05.01.07 | Drainage furrows and channels | No. | 5
PSDB 8.3.5 | 2.05.02 | b) Services that adjoin a trench
| 2.05.02.01 | Water pipes up to DN 200 | m | 100
| 2.05.02.02 | Water mains DN 250 and larger | m | 50
| 2.05.02.03 | Sewer pipes up to DN 160 | m | 100
| 2.05.02.04 | Sewer mains DN 200 and larger | m | 50
| 2.05.02.05 | Stormwater pipes (any size) | m | 100
| 2.05.02.06 | Cables (Electrical, data or telephone) | m | 100
| 2.05.02.07 | Drainage furrows and channels | m | 60
PSDB 8.3.5 c | 2.06.03 | c) Services that require special care
| 2.06.03.01 | Crossing underneath power lines up to 11 kV | No. | 1
| 2.06.03.02 | Crossing underneath power lines up to 300 kV | No. | 1
| 2.06.03.03 | Crossing underneath telephone lines | No. | 4
| 2.06.02.04 | Working alongside electricity poles | No. | 15
| 2.06.02.05 | Working alongside telephone poles | No. | 5
| 2.06.02.06 | Working alongside traffic signals | No. | 4
| 2.06.02.07 | Working alongside street lights | No. | 40
Carried forward
Part B - Section 2: DN 600 Steel Bypass Pipeline
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSDB 8.3.6 | 2.07 | Finishing
PSDB8.3.6.1 | 2.07.01 | Reinstate road surfaces complete with all courses
| 2.07.01.01 | a) Gravel on shoulders | m² | 45
| 2.07.01.02 | b) Asphalt of thickness 40 mm in parking area | m² | 100
| 2.07.01.03 | c) Asphalt of thickness 40 mm in roadway | m² | 700
| 2.07.01.04 | d) Re-instatement of unreinforced concrete | m² | 60
| 2.07.01.05 | e) Re-instatement of reinforced concrete | m³ | 60
| 2.07.01.06 | f) Re-instatement of bricks, concrete pre-cast units and interlocking concrete segmental paving | m² | 100
| 2.07.01.07 | g) Re-instatement of grouted brick paving, complete | m² | 50
| 2.07.01.08 | h) Re-instatement of gardens, lawns and grassing | m² | 50
PSDB8.3.6.2 | 2.07.02 | Reinstatement of surfacing for walkways
| 2.07.02.01 | a) Re-instatement of walkways with unreinforced concrete | m² | 60
| 2.07.02.02 | b) Re-instatement of walkways with interlocking concrete segmental paving | m² | 360
PSDB8.3.6.3 | 2.07.03 | Reinstatement of kerbs and channels
|  | a) Re-instatement of all types of precast kerbing, complete | m | 200
|  | b) Re-instatement of precast concrete gutter, complete | m | 150
|  | c) Re-instatement of all types of insitu cast concrete kerbing, complete | m | 100
|  | d) Re-instatement of all types of insitu cast concrete gutter, complete | m | 150
PSDB 8.3.7 | 2.08 | Accommodation of traffic | sum | 1
Carried forward to summary (Part B - Section 2)
Part B - Section 2: DN 600 Steel Bypass Pipeline
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 L | 3 | MEDIUM-PRESSURE PIPELINES
Refer to Drawing: JW14358-16941-T-012-S11-00-TMS
PSL 8.2.16 | 3.01 | Supply, Lay and Bed Steel Pipes Complete with
Welded Joints
| 3.01.01 | DN 600 welded steel; 6 mm wall thickness; convex heat | m | 510
sink steel ring joint; API 5L X42 steel pipe, with Rigid
Polyurethane Coating (RPU) and Solvent Free Liquid
Epoxy lining (SFE). Bedded and jointing as per
Drawing: JW14358-16941-T-017-S05-00-TMS
Drawing: JW14358-16941-T-017-S16-00-TMS
PSL 8.2.19 | 3.02 | Extra over 3.01 for the Supplying, Laying, Welding
or Jointing and Bedding of Steel specials
| 3.02.01 | DN 600 steel; 6 mm wall thickness; API 5LX42 steel,
long radius bends, with Rigid Polyurethane Coating
(RPU) and Solvent Free Liquid Epoxy lining (SFE):
| 3.02.01.01 | Item 1: DN 600, 46° up to 90°, 5 segment bend to | No. | 3
SANS 719; centre line radius R = 1220 mm, unflanged
| 3.02.01.02 | Item 2: DN 600, 23° up to 45°, 3 segment bend to | No. | 2
SANS 719; centre line radius R = 1220 mm, unflanged
| 3.02.01.03 | Item 3: DN 600, 11.25 up to 22.5°, 2 segment bend to | No. | 2
SANS 719; centre line radius R = 1220 mm, unflanged
| 3.02.02 | Mitres up to 11.25° | No. | 4
| 3.02.03 | DN 600 loose flanges to SANS 1123 table 1600/3 for | No. | 6
welding on site
PSL 8.2.22 | 3.03 | Flushing and sterilising of pipelines
| 3.03.01 | DN 600 steel pipe | m | 510
PSL 8.2.23 | 3.04 | Hydraulic field-testing of pipelines
| 3.04.01 | DN 600 steel pipe | m | 510
PSL 8.2.24 | 3.05 | Pipeline and Valve Markers
| 3.05.01 | a) Precast Concrete Marker | No. | 10
(Drawing: JW14358-16941-T-017-S07-00-TMS)
| 3.05.02 | b) Kerb Marking | No. | 10
(Drawing: JW14358-16941-T-017-S07-00-TMS)
Carried forward to summary (Part B - Section 2)
Part B - Section 2: DN 600 Steel Bypass Pipeline
Bedding (pipes)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 LB | 4 | BEDDING (PIPES)
Refer to Drawing:
JW14358-16941-T-012-S11-00-TMS
PSLB 8.2.1.1 | 4.01 | Provision of bedding from trench excavations
without the need for screening or other treatments
| 4.01.01 | Selected granular material | m³ | 30
| 4.01.02 | Selected fill material | m³ | 60
PSLB 8.2.1.2 | 4.02 | Provision of bedding from trench excavations including screening or other treatments
| 4.02.01 | Selected granular material | m³ | 60
| 4.02.02 | Selected fill material | m³ | 40
8.2.2 | 4.03 | Supply only of bedding by importation
| 4.03.01 | From other necessary excavations (Provisional)
| 4.03.01.01 | Selected granular material | m³ | 20
| 4.03.01.02 | Selected fill material | m³ | 20
| 4.03.02 | From commercial sources (Provisional)
| 4.03.02.01 | Selected granular material | m³ | 370
| 4.03.02.02 | Selected fill material | m³ | 40
8.2.4 | 4.04 | Encasing of pipes in concrete
| 4.04.01 | Encasing DN 600 steel pipe
| 4.04.01.01 | Class 15 MPa/19 mm | m³ | 10
| 4.04.01.02 | Class 30 MPa/19 mm | m³ | 5
PSLB 8.2.6 | 4.05 | Extra over items 4.01 and 4.02 for bedding stabilized | m³ | 40
with 5% cement
PSLB 8.2.7 | 4.06 | Compaction Testing using a Nuclear Moisture | No. | 10
Density Gauge
Carried forward to summary (Part B - Section 2)
Part B - Section 2: DN 600 Steel Bypass Pipeline
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SUMMARY
SANS 1200 C |  | SITE CLEARANCE
SANS 1200 DB |  | EARTHWORKS (PIPE TRENCHES)
SANS 1200 L |  | MEDIUM-PRESSURE PIPELINES
SANS 1200 LB |  | BEDDING (PIPES)
Total carried forward to summary

## DN 800
Part B - Section 3: DN 800 Steel Pipeline
Site clearance
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 C | 1 | SITE CLEARANCE
Refer to Drawing:
JW14358-16941-T-012-S14-00-TMS
PSC 8.2.1 | 1.01 | Clear and Grub
| 1.01.01 | Strips, 3 m wide | m | 120
8.2.2 | 1.02 | Remove and grub large trees and tree stumps
of girth
| 1.02.01 | Over 1 m and up to and including 2 m | No. | 2
| 1.02.02 | Over 2 m and up to and including 3 m | No. | 2
PSC 8.2.5 | 1.03 | Take down existing fences, guardrails and
masonry walls
| 1.03.01 | a) Guardrails | m | 30
| 1.03.02 | b) Diamond mesh fencing | m | 20
| 1.03.03 | c) Steel palisade fencing | m | 10
| 1.03.04 | d) Clearview fencing | m | 20
| 1.03.05 | e) 110 mm masonry wall | m | 10
| 1.03.06 | f) 220 mm masonry wall | m | 10
8.2.10 | 1.04 | Remove topsoil to nominal depth of 150 mm and stockpile | m³ | 54
PSC 8.2.11 | 1.05 | Temporary fencing or hoarding
| 1.05.01 | a) 1.8 m High Diamond mesh fencing | m | 100
PSC 8.2.12 | 1.06 | Removal of man-made surfaces and kerbing
| 1.06.01 | a) Road materials with Asphalt ≤ 50mm thick | m² | 20
| 1.06.02 | b) Road materials with Asphalt > 50 ≤ 100mm thick | m² | 40
| 1.06.03 | c) Interlocking concrete segmental paving blocks, | m² | 40
Class 2.6/40MPa (all colours)
| 1.06.04 | d) Concrete paving blocks, Class 2.6/40MPa | m² | 20
(various sizes)
| 1.06.05 | e) Brick paving | m² | 20
| 1.06.06 | f) Unreinforced concrete ≤ 75mm thick | m² | 20
| 1.06.07 | g) Reinforced concrete ≤ 75mm thick | m² | 20
| 1.06.08 | h) Garden, lawns and grassing | m² | 40
| 1.06.09 | i) All types of Kerbing including channel | m | 50
Carried forward
Part B - Section 3: DN 800 Steel Pipeline
Site clearance
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSC 8.2.13 | 1.07 | Backfilling and reinstatement of man-made surfaces re-using removed materials
| 1.07.01 | a) Interlocking concrete segmental paving blocks, Class 2.6/40MPa (all colours) | m² | 40
| 1.07.02 | b) Concrete paving blocks, Class 2.6/40MPa (various sizes) | m² | 20
| 1.07.03 | c) Brick paving | m² | 20
| 1.07.04 | d) Kerbing (all types of kerbing) | m | 50
PSC 8.2.14 | 1.08 | Take down and re-erect existing fences and guardrails
| 1.08.01 | a) Guardrails | m | 30
| 1.08.02 | b) Diamond mesh fencing | m | 10
| 1.08.03 | c) Steel palisade fencing | m | 10
| 1.08.04 | d) Clearview fencing | m | 10
PSC 8.2.15 | 1.09 | Reinstatement of existing masonry walls and steel fences
PSC 8.2.15.1 | 1.09.1 | Face brick walls
| 1.09.1.1 | a) 110 mm wall | m² | 10
| 1.09.1.2 | b) 220 mm wall | m² | 10
PSC 8.2.15.2 | 1.09.2 | Plastered walls
| 1.09.2.01 | a) 110 mm wall | m² | 10
| 1.09.2.02 | b) 220 mm wall | m² | 10
PSC 8.2.15.3 | 1.10.3 | Steel fences
| 1.10.3.01 | a) Palisade fencing | m² | 10
| 1.10.3.02 | b) Clearview fencing | m² | 10
PSC 8.2.16 | 1.11 | Protection of trees | No | 6
PSC 8.2.21 | 1.11 | Temporary removal and reinstatement of electrical infrastructure
| 1.11.01 | a) Electrical Poles | No | 1
| 1.11.02 | b) Street Lights | No | 1
Carried forward to summary (Part B - Section 3)
Part B - Section 3: DN 800 Steel Pipeline
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 DB | 2 | EARTHWORKS (PIPE TRENCHES)
Refer to Drawing:
JW14358-16941-T-012-S14-00-TMS
PSDB 8.3.2 | 2.01 | a) Excavate in all materials, for trenches, backfill
compact and dispose of surplus material
| 2.01.01 | Pipes of diameter of DN 800 for depths:
| 2.01.01.01 | Up to 1,0 m | m | 10
| 2.01.01.02 | Over 1,0 m up to 2,0 m | m | 10
| 2.01.01.03 | Over 2,0 m up to 3,0 m | m | 105
| 2.01.01.04 | Over 3,0 m up to 4,0 m | m | 10
PSDB 8.3.2 | 2.02 | b) Extra over item 2.01 above for:
| 2.02.01 | 1) Intermediate excavation | m³ | 50
| 2.02.02 | 2) Hard rock excavation | m³ | 50
| 2.02.03 | 3) Hand excavation where ordered by the Project Manager
| 2.02.03.01 | a) Soft material | m³ | 50
| 2.02.03.02 | b) Intermediate material | m³ | 50
| 2.02.03.03 | c) Hard material | m³ | 30
PSDB 8.3.2 | 2.02.04 | 4) Backfill stabilized with 5% cement where directed by the Project Manager | m³ | 100
PSDB 8.3.2 | 2.02.05 | 5) Soilcrete backfill where directed by the Project Manager | m³ | 100
8.3.2 | 2.02.06 | c) Excavate and dispose of unsuitable material from trench bottom (provisional) | m³ | 80
8.3.3 | 2.03 | Excavation Ancillaries
8.3.3.1 | 2.03.01 | Make up deficiency in backfill material
| 2.03.01.01 | a) from other necessary excavations on site | m³ | 60
| 2.03.01.02 | c) by importation from commercial or off-site sources selected by the contractor | m³ | 60
PSDB 8.3.3.3 | 2.03.02 | Compaction in roadways | m³ | 105
PSDB 8.3.4 | 2.04 | Particular Items
PSDB 8.3.4 (a) | 2.04.01 | a) Shore trench opposite structure or service | m | 100
PSDB 8.3.4 (c) | 2.04.02 | Dealing with groundwater
| 2.04.02.01 | (1) Crushed stone (14 mm or 20 mm) | m³ | 20
| 2.04.02.02 | (2) Nonwoven, needle punched, continuous filament, | m2 | 200
polyester Geotextile
Carried forward
Part B - Section 3: DN 800 Steel Pipeline
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSDB 8.3.5 | 2.05 | Existing Services that Intersect or Adjoin
a Pipe Trench
PSDB 8.3.5 | 2.05.01 | a) Services that intersect a trench
| 2.05.01.01 | Water pipes up to DN 200 | No. | 2
| 2.05.01.02 | Water mains DN 250 and larger | No. | 1
| 2.05.01.03 | Sewer pipes up to DN 160 | No. | 2
| 2.05.01.04 | Sewer mains DN 200 and larger | No. | 1
| 2.05.01.05 | Stormwater pipes (any size) | No. | 2
| 2.05.01.06 | Cables (Electrical, data or telephone) | No. | 5
| 2.05.01.07 | Drainage furrows and channels | No. | 1
PSDB 8.3.5 | 2.05.02 | b) Services that adjoin a trench
| 2.05.02.01 | Water pipes up to DN 200 | m | 20
| 2.05.02.02 | Water mains DN 250 and larger | m | 10
| 2.05.02.03 | Sewer pipes up to DN 160 | m | 20
| 2.05.02.04 | Sewer mains DN 200 and larger | m | 10
| 2.05.02.05 | Stormwater pipes (any size) | m | 30
| 2.05.02.06 | Cables (Electrical, data or telephone) | m | 50
| 2.05.02.07 | Drainage furrows and channels | m | 20
PSDB 8.3.5 c | 2.06.03 | c) Services that require special care
| 2.06.03.01 | Crossing underneath power lines up to 11 kV | No. | 1
| 2.06.03.02 | Crossing underneath power lines up to 300 kV | No. | 1
| 2.06.03.03 | Crossing underneath telephone lines | No. | 2
| 2.06.02.04 | Working alongside electricity poles | No. | 4
| 2.06.02.05 | Working alongside telephone poles | No. | 2
| 2.06.02.06 | Working alongside traffic signals | No. | 2
| 2.06.02.07 | Working alongside street lights | No. | 20
Carried forward
Part B - Section 3: DN 800 Steel Pipeline
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSDB 8.3.6 | 2.07 | Finishing
PSDB8.3.6.1 | 2.07.01 | Reinstate road surfaces complete with all courses
| 2.07.01.01 | a) Gravel on shoulders | m³ | 20
| 2.07.01.02 | b) Asphalt of thickness 40 mm in parking area | m² | 35
| 2.07.01.03 | c) Asphalt of thickness 40 mm in roadway | m² | 65
| 2.07.01.04 | d) Re-instatement of unreinforced concrete | m² | 10
| 2.07.01.05 | e) Re-instatement of reinforced concrete | m³ | 5
| 2.07.01.06 | f) Re-instatement of bricks, concrete pre-cast units and | m² | 20
interlocking concrete segmental paving
| 2.07.01.07 | g) Re-instatement of grouted brick paving, complete | m² | 10
| 2.07.01.08 | h) Re-instatement of gardens, lawns and grassing | m² | 10
PSDB8.3.6.2 | 2.07.02 | Reinstatement of surfacing for walkways
| 2.07.02.01 | a) Re-instatement of walkways with unreinforced concrete | m² | 10
| 2.07.02.02 | b) Re-instatement of walkways with interlocking concrete | m² | 30
segmental paving
PSDB8.3.6.3 | 2.07.03 | Reinstatement of kerbs and channels
|  | a) Re-instatement of all types of precast kerbing, complete | m | 10
|  | b) Re-instatement of precast concrete gutter, complete | m | 10
|  | c) Re-instatement of all types of insitu cast concrete | m | 5
kerbing, complete
|  | d) Re-instatement of all types of insitu cast concrete | m | 5
gutter, complete
PSDB 8.3.7 | 2.08 | Accommodation of traffic | sum | 1
Carried forward to summary (Part B - Section 3)
Part B - Section 3: DN 800 Steel Pipeline
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 L | 3 | MEDIUM-PRESSURE PIPELINES
Refer to Drawing:
JW14358-16941-T-012-S14-00-TMS
PSL 8.2.16 | 3.01 | Supply, Lay and Bed Steel Pipes Complete with
Welded Joints
| 3.03.01 | DN 800 steel; 8 mm wall thickness; API 5L X42 steel | m | 115
pipe; with Rigid Polyurethane Coating (RPU) and
Solvent Free Liquid Epoxy lining (SFE); Bedded as per
Drawing: JW14358-16941-T-017-S05-00-TMS
PSL 8.2.19 | 3.02 | Extra over 3.01 for the Supplying, Laying, Welding
or Jointing and Bedding of Steel specials
| 3.02.01 | DN 800 steel; 8 mm wall thickness; API 5L X42 steel Solvent Free Liquid Epoxy lining (SFE):
long radius bends; with Rigid Polyurethane Coating (RPU)
and Solvent Free Liquid Epoxy lining (SFE); Bedded as
per Drawing: JW14358-16941-T-017-S05-00-TMS
| 3.02.01.01 | Item 1: DN 800, 46° up to 90°, 5 segment bend to | No. | 2
SANS 719; centre line radius R = 1630 mm, unflanged
| 3.02.01.02 | Item 2: DN 800, 23° up to 45°, 3 segment bend to | No. | 2
SANS 719; centre line radius R = 1630 mm, unflanged
| 3.02.01.03 | Item 3: DN 800, 11.25 up to 22.5°, 2 segment bend to | No. | 2
SANS 719; centre line radius R = 1630 mm, unflanged
| 3.02.02 | Mitres up to 11.25° | No. | 4
| 3.02.03 | DN 800 loose flanges to SANS 1123 Table 2500/3 | No. | 4
for welding on site
PSL 8.2.22 | 3.03 | Flushing and sterilising of pipelines
| 3.03.01 | DN 800 steel pipe | m | 115
PSL 8.2.23 | 3.04 | Hydraulic field-testing of pipelines
| 3.04.01 | DN 800 steel pipe | m | 115
PSL 8.2.24 | 3.05 | Pipeline and Valve Markers
| 3.05.01 | a) Precast Concrete Marker | No. | 5
(Drawing JW14358-16941-T-017-S07-00-TMS)
| 3.05.02 | b) Kerb Marking | No. | 5
(Drawing JW14358-16941-T-017-S07-00-TMS)
Carried forward to summary (Part B - Section 3)
Part B - Section 3: DN 800 Steel Pipeline
Bedding (pipes)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 LB | 4 | BEDDING (PIPES)
Refer to Drawing:
JW14358-16941-T-012-S14-00-TMS
PSLB 8.2.1.1 | 4.01 | Provision of bedding from trench excavations
without the need for screening or other treatments
| 4.01.01 | Selected granular material | m³ | 10
| 4.01.02 | Selected fill material | m³ | 15
PSLB 8.2.1.2 | 4.02 | Provision of bedding from trench excavations
including screening or other treatments
| 4.02.01 | Selected granular material | m³ | 10
| 4.02.02 | Selected fill material | m³ | 15
8.2.2 | 4.03 | Supply only of bedding by importation
| 4.03.01 | From other necessary excavations (Provisional)
| 4.03.01.01 | Selected granular material | m³ | 10
| 4.03.01.02 | Selected fill material | m³ | 10
| 4.03.01 | From commercial sources (Provisional)
| 4.03.01.01 | Selected granular material | m³ | 110
| 4.03.01.02 | Selected fill material | m³ | 20
8.2.4 | 4.04 | Encasing of pipes in concrete
| 4.04.01 | Encasing DN 800 steel pipe
| 4.04.01.01 | Class 15 MPa/19 mm | m³ | 20
| 4.04.01.02 | Class 30 MPa/19 mm | m³ | 10
PSLB 8.2.6 | 4.05 | Extra over items 4.01 and 4.02 for bedding stabilized | m³ | 30
with 5% cement
PSLB 8.2.7 | 4.06 | Compaction Testing using a Nuclear Moisture Density | No. | 6
Gauge
Carried forward to summary (Part B - Section 3)
Part B - Section 3: DN 800 Steel Pipeline
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SUMMARY
SANS 1200 C |  | SITE CLEARANCE
SANS 1200 DB |  | EARTHWORKS (PIPE TRENCHES)
SANS 1200 L |  | MEDIUM-PRESSURE PIPELINES
SANS 1200 LB |  | BEDDING (PIPES)
Total carried forward to summary

## DN200 mPVC
Part B - Section 4: DN 200 High Impact mPVC Pipeline
Site clearance
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 C | 1 | SITE CLEARANCE
Refer to Drawing: JW14358-16941-T-012-S13-00-TMS & JW14358-16941-T-012-S13-00-TMS
JW14358-16941-T-012-S13-00-TMS
PSC 8.2.1 | 1.01 | Clear and Grub
| 1.01.02 | Strips, 2 m wide | m | 830
8.2.2 | 1.02 | Remove and grub large trees and tree stumps of
girth
| 1.02.01 | Over 1 m and up to and including 2 m | No. | 5
| 1.02.02 | Over 2 m and up to and including 3 m | No. | 8
PSC 8.2.5 | 1.03 | Take down existing fences, guardrails and masonry
walls
| 1.03.01 | a) Guardrails | m | 120
| 1.03.02 | b) Diamond mesh fencing | m | 80
| 1.03.03 | c) Steel palisade fencing | m | 20
| 1.03.04 | d) Clearview fencing | m | 60
| 1.03.05 | e) 110 mm masonry wall | m | 40
| 1.03.06 | f) 220 mm masonry wall | m | 40
8.2.10 | 1.04 | Remove topsoil to nominal depth of 150 mm and stockpile | m³ | 250
PSC 8.2.11 | 1.05 | Temporary fencing or hoarding
|  | a) 1.8 m High Diamond mesh fencing | m | 400
PSC 8.2.12 | 1.06 | Removal of man-made surfaces and kerbing
| 1.06.01 | a) Road materials with Asphalt ≤ 50mm thick | m² | 100
| 1.06.02 | b) Road materials with Asphalt > 50 ≤ 100mm thick | m² | 200
| 1.06.03 | c) Interlocking concrete segmental paving blocks, | m² | 100
Class 2.6/40MPa (all colours)
| 1.06.04 | d) Concrete paving blocks, Class 2.6/40MPa | m² | 50
(various sizes)
| 1.06.05 | e) Brick paving | m² | 50
| 1.06.06 | f) Unreinforced concrete ≤ 75mm thick | m² | 50
| 1.06.07 | g) Reinforced concrete ≤ 75mm thick | m² | 50
| 1.06.08 | h) Garden, lawns and grassing | m² | 200
| 1.06.09 | i) All types of Kerbing including channel | m | 400
Carried forward
Part B - Section 4: DN 200 High Impact mPVC Pipeline
Site clearance
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSC 8.2.13 | 1.07 | Backfilling and reinstatement of man-made surfaces
re-using removed materials
| 1.07.01 | a) Interlocking concrete segmental paving blocks, | m² | 100
Class 2.6/40MPa (all colours)
| 1.07.02 | b) Concrete paving blocks, Class 2.6/40MPa | m² | 50
(various sizes)
| 1.07.03 | c) Brick paving | m² | 50
| 1.07.04 | d) Kerbing (all types of kerbing) | m | 200
PSC 8.2.14 | 1.08 | Take down and re-erect existing fences and
guardrails
| 1.08.01 | a) Guardrails | m | 200
| 1.08.02 | b) Diamond mesh fencing | m | 100
| 1.08.03 | c) Steel palisade fencing | m | 50
| 1.08.04 | d) Clearview fencing | m | 50
PSC 8.2.15 | 1.09 | Reinstatement of existing masonry walls and steel
fences
PSC 8.2.15.1 | 1.09.1 | Face brick walls
| 1.09.1.1 | a) 110 mm wall | m² | 20
| 1.09.1.2 | b) 220 mm wall | m² | 20
PSC 8.2.15.2 | 1.09.2 | Plastered walls
| 1.09.2.01 | a) 110 mm wall | m² | 20
| 1.09.2.02 | b) 220 mm wall | m² | 20
PSC 8.2.15.3 | 1.09.3 | Steel fences
| 1.09.3.01 | a) Palisade fencing | m² | 20
| 1.09.3.02 | b) Clearview fencing | m² | 20
PSC 8.2.16 | 1.10 | Protection of trees | No | 8
PSC 8.2.21 | 1.11 | Temporary removal and reinstatement of electrical
infrastructure
| 1.11.01 | a) Electrical Poles | No | 10
| 1.11.02 | b) Street Lights | No | 8
Carried forward to summary (Part - Section 4)
Part B - Section 4: DN 200 High Impact mPVC Pipeline
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 DB | 2 | EARTHWORKS (PIPE TRENCHES)
Refer to Drawing: JW14358-16941-T-012-S13-00-TMS & JW14358-16941-T-012-S13-00-TMS
JW14358-16941-T-012-S13-00-TMS
PSDB 8.3.2 | 2.01 | a) Excavate in all materials, for trenches, backfill
compact and dispose of surplus material
| 2.01.02 | Pipes of diameter of DN 200 for depths:
| 2.01.02.01 | Up to 1,0 m | m | 20
| 2.01.02.02 | Over 1,0 m up to 2,0 m | m | 680
| 2.01.02.03 | Over 2,0 m up to 3,0 m | m | 120
PSDB 8.3.2 | 2.02 | b) Extra over item 2.01 above for:
| 2.02.01 | 1) Intermediate excavation | m³ | 120
| 2.02.02 | 2) Hard rock excavation | m³ | 120
| 2.02.03 | 3) Hand excavation where ordered by the Project Manager
| 2.02.03.01 | a) Soft material | m³ | 120
| 2.02.03.02 | b) Intermediate material | m³ | 120
| 2.02.03.03 | c) Hard material | m³ | 120
PSDB 8.3.2 | 2.02.04 | 4) Backfill stabilized with 5% cement where directed by | m³ | 240
the Project Manager
PSDB 8.3.2 | 2.02.05 | 5) Soilcrete backfill where directed by the Project Manager | m³ | 240
8.3.2 | 2.02.06 | c) Excavate and dispose of unsuitable material from | m³ | 80
trench bottom (provisional)
8.3.3 | 2.03 | Excavation Ancillaries
8.3.3.1 | 2.03.01 | Make up deficiency in backfill material
| 2.03.01.01 | a) from other necessary excavations on site | m³ | 60
| 2.03.01.02 | c) by importation from commercial or off-site sources | m³ | 60
selected by the contractor
PSDB 8.3.3.3 | 2.03.02 | Compaction in roadways | m³ | 200
PSDB 8.3.4 | 2.04 | Particular Items
PSDB 8.3.4 (a) | 2.04.01 | a) Shore trench opposite structure or service | m | 200
PSDB 8.3.4 (c) | 2.04.02 | Dealing with groundwater
| 2.04.02.01 | (1) Crushed stone (14 mm or 20 mm) | m³ | 50
| 2.04.02.02 | (2) Nonwoven, needle punched, continuous filament, | m2 | 450
polyester Geotextile
Carried forward
Part B - Section 4: DN 200 High Impact mPVC Pipeline
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSDB 8.3.5 | 2.05 | Existing Services that Intersect or Adjoin a Pipe
Trench
PSDB 8.3.5 | 2.05.01 | a) Services that intersect a trench
| 2.05.01.01 | Water pipes up to DN 200 | No. | 8
| 2.05.01.02 | Water mains DN 250 and larger | No. | 4
| 2.05.01.03 | Sewer pipes up to DN 160 | No. | 8
| 2.05.01.04 | Sewer mains DN 200 and larger | No. | 4
| 2.05.01.05 | Stormwater pipes (any size) | No. | 10
| 2.05.01.06 | Cables (Electrical, data or telephone) | No. | 25
| 2.05.01.07 | Drainage furrows and channels | No. | 5
PSDB 8.3.5 | 2.05.02 | b) Services that adjoin a trench
| 2.05.02.01 | Water pipes up to DN 200 | m | 120
| 2.05.02.02 | Water mains DN 250 and larger | m | 50
| 2.05.02.03 | Sewer pipes up to DN 160 | m | 120
| 2.05.02.04 | Sewer mains DN 200 and larger | m | 50
| 2.05.02.05 | Stormwater pipes (any size) | m | 120
| 2.05.02.06 | Cables (Electrical, data or telephone) | m | 150
| 2.05.02.07 | Drainage furrows and channels | m | 60
PSDB 8.3.5 c | 2.06.03 | c) Services that require special care
| 2.06.03.01 | Crossing underneath power lines up to 11 kV | No. | 1
| 2.06.03.02 | Crossing underneath power lines up to 300 kV | No. | 1
| 2.06.03.03 | Crossing underneath telephone lines | No. | 4
| 2.06.02.04 | Working alongside electricity poles | No. | 15
| 2.06.02.05 | Working alongside telephone poles | No. | 5
| 2.06.02.06 | Working alongside traffic signals | No. | 4
| 2.06.02.07 | Working alongside street lights | No. | 50
Carried forward
Part B - Section 4: DN 200 High Impact mPVC Pipeline
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSDB 8.3.6 | 2.07 | Finishing
PSDB8.3.6.1 | 2.07.01 | Reinstate road surfaces complete with all courses
| 2.07.01.01 | a) Gravel on shoulders | m³ | 45
| 2.07.01.02 | b) Asphalt of thickness 40 mm in parking area | m² | 100
| 2.07.01.03 | c) Asphalt of thickness 40 mm in roadway | m² | 200
| 2.07.01.04 | d) Re-instatement of unreinforced concrete | m² | 60
| 2.07.01.05 | e) Re-instatement of reinforced concrete | m³ | 60
| 2.07.01.06 | f) Re-instatement of bricks, concrete pre-cast units and | m² | 100
interlocking concrete segmental paving
| 2.07.01.07 | g) Re-instatement of grouted brick paving, complete | m² | 50
| 2.07.01.08 | h) Re-instatement of gardens, lawns and grassing | m² | 400
PSDB8.3.6.2 | 2.07.02 | Reinstatement of surfacing for walkways
| 2.07.02.01 | a) Re-instatement of walkways with unreinforced concrete | m² | 60
| 2.07.02.02 | b) Re-instatement of walkways with interlocking concrete | m² | 360
segmental paving
PSDB8.3.6.3 | 2.07.03 | Reinstatement of kerbs and channels
|  | a) Re-instatement of all types of precast kerbing, complete | m | 300
|  | b) Re-instatement of precast concrete gutter, complete | m | 200
|  | c) Re-instatement of all types of insitu cast concrete | m | 200
kerbing, complete
|  | d) Re-instatement of all types of insitu cast concrete | m | 200
gutter, complete
PSDB 8.3.7 | 2.08 | Accommodation of traffic | sum | 1
Carried forward to summary (Part B - Section 4)
Part B - Section 4: DN 200 High Impact mPVC Pipeline
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 L | 3 | MEDIUM-PRESSURE PIPELINES
Refer to Drawing: JW14358-16941-T-012-S13-00-TMS & JW14358-16941-T-012-S13-00-TMS
JW14358-16941-T-012-S13-00-TMS
PSL 8.2.1 | 3.01 | Supply, Lay, and Bed Pipes Complete with Couplings
| 3.01.01 | High-Impact mPVC Class 16 complete with
shouldered end coupling system
| 3.01.01.01 | Class 16 DN 200 | m | 830
PSL 8.2.20 | 3.02 | Supply, Lay and Bed HDPE Pipes Complete with
Welded Joints
| 3.02.01 | PN16 PE100 HDPE
| 3.02.01.01 | PN16 DN 250 | m | 100
8.2.2 | 3.03 | Extra-over 3.0.1 for the Supplying, Laying, and Bedding of Specials Complete with Couplings
| 3.03.01 | High-Impact mPVC Class 16 bends complete with shouldered end coupling system
| 3.03.01.01 | DN 200, 11.25° bend | No. | 8
| 3.03.01.02 | DN 200, 22.5° bend | No. | 8
| 3.03.01.03 | DN 200, 45° bend | No. | 3
| 3.03.01.04 | DN 200, 90° bend | No. | 3
| 3.03.02 | High-Impact mPVC Class 16 shouldered end repair
couplings
| 3.03.02.01 | DN 200 | No. | 4
| 3.03.04 | Flange adaptors for High-Impact mPVC Class 16 complete with shouldered end coupling system
| 3.03.04.01 | DN 200 | No. | 6
PSL 8.2.21 | 3.04 | Extra over 3.02 for the Supplying, Laying, Butt
Fusion Welding and Bedding of HDPE specials
| 3.04.01 | HDPE PN16 PE100 bends
| 3.04.01.01 | DN 250 90° bend | No. | 2
| 3.04.01.02 | DN 250 45° bend | No. | 2
| 3.04.01.03 | DN 250 22.5° bend | No. | 2
| 3.04.01.04 | DN 250 11.25° bend | No. | 2
PSL 8.2.22 | 3.05 | Flushing and sterilising of pipelines
| 3.05.01 | Class 16 DN 200 High-Impact mPVC pipe | m | 830
| 3.05.02 | PN16 PE100 DN250 HDPE | m | 100
Carried forward
Part B - Section 4: DN 200 High Impact mPVC Pipeline
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSL 8.2.23 | 3.06 | Hydraulic field-testing of pipelines
| 3.06.01 | Class 16 DN 200 High-Impact mPVC pipe | m | 830
| 3.06.02 | PN16 PE100 DN 250 HDPE | m | 100
PSL 8.2.24 | 3.07 | Pipeline and Valve Markers
| 3.07.01 | a) Precast Concrete Marker | No. | 8
(Drawing: JW14358-16941-T-017-S07-00-TMS)
| 3.07.02 | b) Kerb Marking | No. | 8
(Drawing JW14358-16941-T-017-S07-00-TMS)
Carried forward to summary (Part B - Section 4)
Part B - Section 4: DN 200 High Impact mPVC Pipeline
Bedding (pipes)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 LB | 4 | BEDDING (PIPES)
Refer to Drawing: JW14358-16941-T-012-S13-00-TMS & JW14358-16941-T-012-S13-00-TMS
JW14358-16941-T-012-S13-00-TMS
PSLB 8.2.1.1 | 4.01 | Provision of bedding from trench excavations
without the need for screening or other treatments
| 4.01.01 | Selected granular material | m³ | 20
| 4.01.02 | Selected fill material | m³ | 120
PSLB 8.2.1.2 | 4.02 | Provision of bedding from trench excavations
including screening or other treatments
| 4.02.01 | Selected granular material | m³ | 20
| 4.02.02 | Selected fill material | m³ | 40
8.2.2 | 4.03 | Supply only of bedding by importation:
| 4.03.01 | From other necessary excavations (Provisional)
| 4.03.01.01 | Selected granular material | m³ | 20
| 4.03.01.02 | Selected fill material | m³ | 20
| 4.03.02 | From commercial sources (Provisional)
| 4.03.02.01 | Selected granular material | m³ | 270
| 4.03.02.02 | Selected fill material | m³ | 40
8.2.4 | 4.04 | Encasing of pipes in concrete
| 4.04.01 | Encasing DN 200 mPVC pipe
| 4.04.01.01 | Class 15 MPa/19 mm | m³ | 10
| 4.04.01.02 | Class 30 MPa/19 mm | m³ | 5
PSLB 8.2.6 | 4.05 | Extra over items 4.01 and 4.02 for bedding stabilized | m³ | 40
with 5% cement
PSLB 8.2.7 | 4.06 | Compaction Testing using a Nuclear Moisture Density | No. | 8
Gauge
Carried forward to summary (Part B - Section 4)
Part B - Section 4: DN 200 High Impact mPVC Pipeline
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SUMMARY
SANS 1200 C |  | SITE CLEARANCE
SANS 1200 DB |  | EARTHWORKS (PIPE TRENCHES)
SANS 1200 L |  | MEDIUM-PRESSURE PIPELINES
SANS 1200 LB |  | BEDDING (PIPES)
Total carried forward to summary

## Scour Valve Chambers-Part C
Part C - Section 1 - Scour Valve Chamber 1 and 2: NA13, NA23, NA41, NA64, NA81, NA95, NB10
Site clearance
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 C | 1 | SITE CLEARANCE
Refer to Drawings:
JW14358-16941-T-012-S13-00-TMS
PSC 8.2.1 | 1.01 | Clear and grub
| 1.01.01 | Areas | m² | 450
8.2.10 | 1.02 | Remove topsoil to nominal depth of 150 mm and stockpile | m³ | 70
PSC 8.2.14 | 1.03 | Take down and re-erect existing fences and
guardrails
| 1.03.01 | a) Guardrails | m | 80
| 1.03.02 | b) Diamond mesh fencing | m | 75
Carried forward to summary (Part C - Section 1)
Part C - Section 1 - Scour Valve Chamber 1 and 2: NA13, NA23, NA41, NA64, NA81, NA95, NB10
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 DB | 2 | EARTHWORKS (PIPE TRENCHES)
Refer to Drawings:
JW14358-16941-T-013-S14-00-TMS
JW14358-16941-T-013-S16-00-TMS
PSDB 8.3.2 | 2.01 | Excavation
| 2.01.01 | d) Excavate in all materials for stormwater inlet and outlet | m³ | 850
structures and for manholes, catchpits, valve chambers
and the like, irrespective of depth, and backfill around
structures
| 2.01.02 | e) Extra over 2.01.01 for excavating in
| 2.01.02.01 | 1) intermediate material | m³ | 100
| 2.01.02.02 | 2) hard material | m³ | 100
| 2.01.03 | f) Hand excavation where ordered by the
Project Manager
| 2.01.03.01 | a) Soft material | m³ | 100
| 2.01.03.02 | b) Intermediate material | m³ | 100
| 2.01.03.03 | c) Hard material | m³ | 100
| 2.01.04 | g) Backfill stabilized with 5% cement where directed by the Project Manager | m³ | 200
| 2.01.05 | h) Soilcrete backfill where directed by the Project Manager | m³ | 200
Carried forward to summary (Part C - Section 1)
Part C - Section 1 - Scour Valve Chamber 1 and 2: NA13, NA23, NA41, NA64, NA81, NA95, NB10
Gabions and pitching
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 DK | 3 | GABIONS AND PITCHING
Refer to Drawing:
JW14358-16941-T-013-S14-00-TMS
8.2.2 | 3.01 | Gabions
| 3.01.01 | Gabion mattresses of galvanized wire, up to 0,3 m deep
| 3.01.01.01 | 60mm x 80mm mesh, 2.2mm diameter wire, | m³ | 15
6 m x 2 m x 0.17 m mattress
8.2.4 | 3.02 | Geotextile
| 3.02.01 | Bidim A4 or approved equivalent | m² | 150
8.2.5 | 3.03 | Pitching
| 3.03.01 | Grouted pitching
| 3.03.01.01 | a) Light pitching | m² | 110
Carried forward to summary (Part C - Section 1)
Part C - Section 1 - Scour Valve Chamber 1 and 2: NA13, NA23, NA41, NA64, NA81, NA95, NB10
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 L | 4 | MEDIUM-PRESSURE PIPELINES
Refer to Drawings:
JW14358-16941-T-013-S15-00-TMS
JW14358-16941-T-013-S16-00-TMS
PSL 8.2.1 | 4.01 | Supply, Lay, and Bed Pipes Complete with Couplings
| 4.01.01 | High-Impact mPVC Class 16 complete with shouldered
end coupling system
| 4.01.01.01 | Class 16 DN 250 | m | 400
8.2.2 | 4.02 | Extra-over 4.0.1 for the Supplying, Laying, and
Bedding of Specials Complete with Couplings
| 4.02.01 | High-Impact mPVC Class 16 bends complete with
shouldered end coupling system
| 4.02.01.01 | DN 250, 11.25° bend | No. | 8
| 4.02.01.02 | DN 250, 22.5° bend | No. | 4
| 4.02.01.03 | DN 250, 45° bend | No. | 3
| 4.02.01.04 | DN 250, 90° bend | No. | 3
| 4.02.02 | High-Impact mPVC Class 16 shouldered end repair
couplings
| 4.02.02.01 | DN 250 | No. | 8
| 4.02.03 | Flange adaptors for High-Impact mPVC Class 16
complete with shouldered end coupling system
| 4.02.03.01 | DN 250 | No. | 8
8.2.3 | 4.03 | Extra-over PSL 8.2.16 for Supplying, Fixing, and
Bedding of Valves
| 4.03.01 | Scour Valve Chamber 1
| 4.03.01.01 | Item 2: DN250 PN16 wedge gate valve for vertical | No. | 6
operation; non rising spindle; anti-clockwise closing to
SANS 664; manually operated; Vosa or similar approved;
both ends flanged; flanges drilled to SANS 1123
Table 1600/3
| 4.03.02 | Scour Valve Chamber 2
| 4.03.02.01 | Item 2: DN250 PN16 wedge gate valve for vertical | No. | 1
operation; non rising spindle; anti-clockwise closing to
SANS 664; manually operated; Vosa or similar approved;
both ends flanged; flanges drilled to SANS 1123
Table 1600/3
Carried forward
Part C - Section 1 - Scour Valve Chamber 1 and 2: NA13, NA23, NA41, NA64, NA81, NA95, NB10
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSL 8.2.19 | 4.04 | Extra over 8.2.16 for the Supplying, Laying, Welding
or Jointing and Bedding of Steel specials
| 4.04.01 | Specials for Scour Valve Chamber 1 as per
Drawing: JW14358-16941-T-013-S15-00-TMS
| 4.04.01.01 | Item 1: Spool piece DN 250; wall thickness t = 6 mm; | No. | 5
flanged both ends to SANS 1123 Table 1600/3,
with puddle flange
| 4.04.01.02 | Item 3: Spool piece DN 250; wall thickness t = 6 mm; | No. | 5
flanged one end to SANS 1123 Table 1600/3,
with puddle flange
| 4.04.01.03 | Item 4: Spool piece DN 250; wall thickness t = 6 mm; | No. | 5
flanged both ends to SANS 1123 Table 1600/3
| 4.04.01.04 | Item 5: DN 250, 45 degree, 3 segment bend, wall | No. | 5
thickness t = 6 mm, both ends flanged to
SANS 1123 Table 1600/3
| 4.04.01.05 | Item 6: Reducing tee piece DN 600 x DN 250 mm; | No. | 5
SANS 719 wall thickness t = 6 mm; Flanged all ends
SANS 1123 Table 1600/3
| 4.04.01.06 | Item 7: Spool piece DN 600 wall thickness t = 6 mm; | No. | 10
one end flanged to SANS 1123 Table 1600/3
| 4.04.02 | Specials for Scour Valve Chamber 2 as per
Drawing JW14358-16941-T-013-S16-00-TMS
| 4.04.02.01 | Item 1: Spool piece DN 250; wall thickness t = 6 mm; | No. | 4
flanged both ends drilled to SANS 1123 Table 1600/3;
with puddle flange
| 4.04.02.02 | Item 4a: Stub flange and backing flange for connecting | No. | 2
DN 250 HDPE pipe; flange drilled to
SANS 1123 Table 1600/3
| 4.04.02.03 | Item 4b: DN 250 Flange adaptor for High-Impact mPVC | No. | 2
Class 16 complete with shouldered end coupling system;
Flange drilled to SANS 1123 Table 1600/3
| 4.04.02.04 | Item 5: DN 250, 45 degree, 3 segment bend, wall | No. | 2
thickness t = 6 mm, both ends flanged to
SANS 1123 Table 1600/3
| 4.04.02.05 | Item 6: Reducing Tee-piece DN 600 x DN 250; wall | No. | 2
thickness t = 6 mm; all ends flanged; flanges drilled to
SANS 1123 Table 1600/3
| 4.04.02.06 | Item 7: Spool piece DN 600; wall thickness t = 6 mm; | No. | 4
one end flanged to SANS 1123 Table 1600/3
| 4.04.02.07 | Item 6: Reducing tee piece DN 600 x DN 250 mm; | No. | 5
SANS 719 wall thickness t = 6 mm; Flanged all ends to
SANS 1123 Table 1600/3
Carried forward
Part C - Section 1 - Scour Valve Chamber 1 and 2: NA13, NA23, NA41, NA64, NA81, NA95, NB10
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 4.04.02.08 | Item 7: Spool piece DN 600 wall thickness t = 6 mm; one | No. | 10
end flanged to SANS 1123 Table 1600/3
| 4.04.03 | Specials for Scour Valve Chamber 2 as per
Drawing: JW14358-16941-T-013-S16-00-TMS
| 4.04.03.01 | Item 1: Spool piece DN 250; wall thickness t = 6 mm; | No. | 4
flanged both ends drilled to SANS 1123 Table 1600/3;
with puddle flange
| 4.04.03.02 | Item 4a: Stub flange and backing flange for connecting | No. | 2
DN 250 HDPE pipe; flange drilled to
SANS 1123 Table 1600/3
| 4.04.03.03 | Item 4b: DN 250 Flange adaptor for High-Impact mPVC | No. | 2
Class 16 complete with shouldered end coupling system;
Flange drilled to SANS 1123 Table 1600/3
| 4.04.03.04 | Item 5: DN 250, 45 degree, 3 segment bend, wall | No. | 2
thickness t = 6 mm, both ends flanged to
SANS 1123 Table 1600/3
| 4.04.03.05 | Item 6: Reducing Tee-piece DN 600 x DN 250; wall | No. | 2
thickness t = 6 mm; all ends flanged; flanges drilled to
SANS 1123 Table 1600/3
| 4.04.03.06 | Item 7: Spool piece DN 600; wall thickness t = 6 mm; | No. | 4
one end flanged to SANS 1123 Table 1600/3
PSL 8.2.34 | 4.05 | Operation and Maintenance Manuals for Valves and Flow Meters
|  | DN250 Wedge Gate Valve (PN16) | Sum | 1
Carried forward to summary (Part C - Section 1)
Part C - Section 1 - Scour Valve Chamber 1 and 2: NA13, NA23, NA41, NA64, NA81, NA95, NB10
Stormwater drainage
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 LE | 5 | STORMWATER DRAINAGE
Refer to Drawing:
JW14358-16941-T-013-S38-TMS
8.2.1 | 5.01 | Supply and Lay Concrete Pipe Culverts on Class B
Bedding
| 5.01.01 | Class 100 D Pipes
| 5.01.01.01 | 300 mm Diameter | m | 20
| 5.01.01.02 | 450 mm Diameter | m | 20
| 5.01.01.03 | 525 mm Diameter | m | 20
| 5.01.01.04 | 600 mm Diameter | m | 20
| 5.01.01.05 | 750 mm Diameter | m | 20
8.2.8 | 5.02 | Supply and Install Manholes, Catchpits, and the like
| 5.02.01 | Precast kerb inlet as per drawing JW14358-16941-T-013-S38-00-TMS | No. | 5
JW14358-16941-T-013-S38-TMS
Carried forward to summary (Part C - Section 1)
Part C - Section 1 - Scour Valve Chamber 1 and 2: NA13, NA23, NA41, NA64, NA81, NA95, NB10
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 2001 | 6 | CONCRETE WORKS (STRUCTURAL)
PART CC1
Refer to Drawing:
JW14358-16941-T-013-S14-TMS
SCHEDULED FORMWORK ITEMS
PSCC1.002 | 6.01 | Smooth
| 6.01.01 | Vertical formwork to
| 6.01.01.01 | Foundations (Floor) | m² | 30
| 6.01.01.02 | Plinths | m² | 7
| 6.01.01.03 | Walls | m² | 550
| 6.01.01.04 | Sump | m² | 21
| 6.01.02 | Horizontal formwork to
| 6.01.02.01 | Precast roof slabs | m² | 85
PSCC1.005 | 6.02 | Narrow widths (up to 300 mm wide)
| 6.02.01 | Vertical Smooth formwork to
| 6.02.01.01 | Precast roof slabs | m | 150
PSCC1.006 | 6.03 | Box out holes/form voids
| 6.03.01 | a) Small, circular, of diameter up to 0,35 m
| 6.03.01.01 | 0 m up to and including 0,5 m | No. | 50
| 6.03.02 | d) Large, other than circular, areas over 0.1 m2 up to 2,0 m2
| 6.03.02.01 | 0 m up to and including 0,5 m | No. | 14
| 6.03.02.02 | Over 2,0 m deep | No. | 14
SCHEDULED REINFORCEMENT ITEMS
PSCC1.007 | 6.04 | Steel bars
| 6.04.01 | a) Steel bars irrespective of grade and diameter | t | 30
PSCC1.008 | 6.05 | High-tensile welded mesh
| 6.05.01 | Mesh Ref 245 | m² | 85
Carried forward
Part C - Section 1 - Scour Valve Chamber 1 and 2: NA13, NA23, NA41, NA64, NA81, NA95, NB10
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
SCHEDULED CONCRETE ITEMS
PSCC1.011 | 6.06 | Blinding layer in Grade 15 MPa/19 mm concrete
| 6.06.01 | 50 mm thickness | m² | 140
PSCC1.012 | 6.07 | Strength concrete
| 6.07.01 | Grade 30 MPa/19 mm concrete in
| 6.07.01.01 | Foundations (Floor) | m³ | 24
| 6.07.01.02 | Plinths | m³ | 4
| 6.07.01.03 | Walls | m³ | 90
| 6.07.01.04 | Roof Slabs | m³ | 18
| 6.07.01.05 | Sump | m3 | 4
PSCC1.013 | 6.08 | Unformed surface finishes
| 6.08.01 | a) Steel-floated finish
| 6.08.01.01 | Foundations (Floor) | m² | 82
| 6.08.01.02 | Plinths | m² | 9
| 6.08.01.03 | Walls | m² | 40
| 6.08.01.04 | Roof Slab | m² | 85
| 6.08.02 | d) Broomed finish
| 6.08.02.01 | Blinding layer | m² | 140
| 6.08.03 | e) Screed in 3:1 Sand and Cement Mix
| 6.08.03.01 | Chamber floor screed | m³ | 8
PSCC1.016 | 6.09 | Joints
| 6.09.01 | Polysulphide sealant between precast slabs | m | 30
PSCC1.018 | 6.10 | Grouting
| 6.10.01 | a) Under bases of pipe supports and straps | m³ | 5
| 6.10.01 | c) Pipe box-outs | m³ | 5
Carried forward
Part C - Section 1 - Scour Valve Chamber 1 and 2: NA13, NA23, NA41, NA64, NA81, NA95, NB10
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.019 | 6.11 | HD bolts and miscellaneous metal work
| 6.11.01 | Metal work for Scour Valve Chamber 1 as per
Drawing: JW14358-16941-T-013-S14-00-TMS
| 6.11.01.01 | Fabricate and install galvanised mild steel ladders as per | No. | 10
Drawing: JW14358-16941-T-017-S09-00-TMS
| 6.11.01.02 | Fabricate and cast in long inlet airvent as per | No. | 5
Drawing: JW14358-16941-T-017-S09-00-TMS
| 6.11.01.03 | Fabricate and cast in short outlet airvent as per | No. | 5
Drawing: JW14358-16941-T-017-S09-00-TMS
| 6.11.01.04 | Fabricate and cast in galvanised access manholes as per | No. | 10
Drawing: JW14358-16941-T-017-S09-00-TMS
| 6.11.01.05 | Fabricate and cast in galvanised acour overflow frame | No. | 5
| 6.11.01.06 | Fabricate and cast in lifting hooks as per bolt detail on | No. | 40
Drawing: JW14358-16941-T-017-S10-00-TMS
| 6.11.02 | Metal work for Scour Valve Chamber 2 as per
Drawing: JW14358-16941-T-013-S16-00-TMS
| 6.11.02.01 | Fabricate and install galvanised mild steel ladders as per | No. | 2
Drawing: JW14358-16941-T-017-S09-00-TMS
| 6.11.02.02 | Fabricate and cast in long inlet airvent as per | No. | 2
Drawing: JW14358-16941-T-017-S09-00-TMS
| 6.11.02.03 | Fabricate and cast in short outlet airvent as per | No. | 2
Drawing: JW14358-16941-T-017-S09-00-TMS
| 6.11.02.04 | Fabricate and cast in galvanised access manholes as per | No. | 2
Drawing: JW14358-16941-T-017-S09-00-TMS
| 6.11.02.05 | Fabricate and cast in lifting hooks as per bolt detail on | No. | 16
Drawing: JW14358-16941-T-017-S10-00-TMS
| 6.11.03 | Metal work for Welling Chamber Type 1 as per
Drawing: JW14358-16941-T-013-S28-00-TMS
| 6.11.03.01 | Fabricate and install galvanised mild steel ladders as per | No. | 2
Drawing: JW14358-16941-T-017-S09-00-TMS
| 6.11.03.02 | Fabricate and cast in galvanised access manholes as per | No. | 2
Drawing: JW14358-16941-T-017-S09-00-TMS
| 6.11.03.03 | Fabricate and cast in lifting hooks as per bolt detail on | No. | 20
Drawing: JW14358-16941-T-017-S10-00-TMS
Carried forward
Part C - Section 1 - Scour Valve Chamber 1 and 2: NA13, NA23, NA41, NA64, NA81, NA95, NB10
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.020 | 6.12 | Colour Mitigation
| 6.12.01 | Exposed Chambers along roadways | m² | 70
MISCELLANEOUS ITEMS
PSCC1.021 | 6.13 | Polythene sheeting under concrete
| 6.13.01 | 250 micron green medium density polyethylene | m² | 85
dampproof sheeting
PSCC1.023 | 6.14 | FRP items
| 6.14.01 | c) FRP Grating
| 6.14.01.01 | 450 mm x 450 mm x 38 mm deep FRP grating | No. | 7
PSCC1.024 | 6.15 | Casting pipes and specials in concrete
| 6.15.01 | DN 250 Steel pipe cast into chamber wall | No. | 14
PSCC1.025 | 6.16 | Installation of precast elements
| 6.16.01 | Precast roof slabs as per | No. | 12
Drawing: JW14358-16941-T-013-S14-00-TMS
| 6.16.02 | Precast roof slabs as per | No. | 2
Drawing: JW14358-16941-T-013-S16-00-TMS
PSCC1.026 | 6.17 | Drilling cores through concrete
| 6.17.01 | 100 mm diameter core through 250 mm thick | No. | 7
concrete slab
Carried forward to summary (Part C - Section 1)
Part C - Section 1 - Scour Valve Chamber 1 and 2: NA13, NA23, NA41, NA64, NA81, NA95, NB10
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SUMMARY
SANS 1200 C |  | SITE CLEARANCE
SANS 1200 DB |  | EARTHWORKS (PIPE TRENCHES)
SANS 1200 DK |  | GABIONS AND PITCHING
SANS 1200 L |  | MEDIUM-PRESSURE PIPELINES
SANS 1200 LE |  | STORMWATER DRAINAGE
SANS 2001 CC1 |  | CONCRETE WORKS (STRUCTURAL)
Total carried forward to summary

## Air Valve-Chamber-Part C
Part C - Section 2 - Air Valve Chambers: Nodes NA15,21,39,45,57,69,85,94,97, NC11
Site clearance
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 C | 1 | SITE CLEARANCE
Refer to Drawings:
JW14358-16941-T-013-S03-00-TMS
JW14358-16941-T-013-S05-00-TMS
JW14358-16941-T-013-S07-00-TMS
JW14358-16941-T-013-S09-00-TMS
JW14358-16941-T-013-S12-00-TMS
PSC 8.2.1 | 1.01 | Clear and grub
| 1.01.01 | Areas | m² | 225
8.2.10 | 1.02 | Remove topsoil to nominal depth of 150 mm and stockpile | m² | 144
PSC 8.2.14 | 1.03 | Take down and re-erect existing fences and guardrails
| 1.03.01 | a) Guardrails | m | 45
| 1.03.02 | b) Diamond mesh fencing | m | 25
Carried forward to summary (Part C - Section 2)
Part C - Section 2 - Air Valve Chambers: Nodes NA15,21,39,45,57,69,85,94,97, NC11
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 DB | 2 | EARTHWORKS (PIPE TRENCHES)
Refer to Drawings: JW14358-16941-T-013-S03-00-TMS, JW14358-16941-T-013-S05-00-TMS, JW14358-16941-T-013-S07-00-TMS, JW14358-16941-T-013-S09-00-TMS, JW14358-16941-T-013-S12-00-TMS
JW14358-16941-T-013-S03-00-TMS
JW14358-16941-T-013-S05-00-TMS
JW14358-16941-T-013-S07-00-TMS
JW14358-16941-T-013-S09-00-TMS
JW14358-16941-T-013-S12-00-TMS
PSDB 8.3.2 | 2.01 | Excavation
| 2.01.01 | d) Excavate in all materials for stormwater inlet and outlet | m³ | 1320
structures and for manholes, catchpits, valve chambers
and the like, irrespective of depth, and backfill around
structures
| 2.01.02 | e) Extra over 2.01.01 for excavating in
| 2.01.02.01 | 1) intermediate material | m³ | 135
| 2.01.02.02 | 2) hard material | m³ | 135
| 2.01.03 | f) Hand excavation where ordered by the Project Manager
| 2.01.03.01 | a) Soft material | m³ | 135
| 2.01.03.02 | b) Intermediate material | m³ | 135
| 2.01.03.03 | c) Hard material | m³ | 135
| 2.01.04 | g) Backfill stabilized with 5% cement where directed by | m³ | 270
the Project Manager
| 2.01.05 | h) Soilcrete backfill where directed by the Project Manager | m³ | 270
Carried forward to summary (Part C - Section 2)
Part C - Section 2 - Air Valve Chambers: Nodes NA15,21,39,45,57,69,85,94,97, NC11
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 L | 3 | MEDIUM-PRESSURE PIPELINES
Refer to Drawings:
JW14358-16941-T-013-S04-00-TMS
JW14358-16941-T-013-S06-00-TMS
JW14358-16941-T-013-S08-00-TMS
JW14358-16941-T-013-S10-00-TMS
JW14358-16941-T-013-S13-00-TMS
8.2.3 | 3.01 | Extra-over PSL 8.2.1 or PSL 8.2.16 for Supplying, Fixing, and Bedding of Valves
| 3.01.01 | DN 600 Air Valve Chamber 1 as per
Drawing: JW14358-16941-T-013-S04-00-TMS
| 3.01.01.01 | Item 5: DN 100 PN16 Resilient Seal Gate Valve; | No. | 1
Non rising spindle; anti-clockwise closing to SANS 664;
manually operated; both ends flanged; flanges drilled
to SANS 1123 Table 1600/3
| 3.01.01.02 | Item 6: DN 100 PN16 Double orifice with anti-shock orifice | No. | 1
mechanism air release valve, Vent-O-Mat RBX or similar
approved; flanges drilled to SANS 1123 Table 1600/3
| 3.01.02 | DN 200 Air Valve Chamber 2 as per
Drawing: JW14358-16941-T-013-S06-00-TMS
| 3.01.02.01 | Item 5: DN 100 PN16 Resilient Seal Gate Valve; Non rising spindle; anti-clockwise closing to SANS 664; | No. | 2
Non rising spindle; anti-clockwise closing to SANS 664;
manually operated; both ends flanged; flanges drilled
to SANS 1123 Table 1600/3
| 3.01.02.02 | Item 6: DN 100 PN16 Double orifice with anti-shock orifice | No. | 2
mechanism air release valve, Vent-O-Mat RBX or similar
approved; flanges drilled to SANS 1123 Table 1600/3
| 3.01.02.03 | Item 8: DN 200 PN16 Wedge Gate Valve; Non rising | No. | 1
spindle; anti-clockwise closing to SANS 664; manually
operated; both ends flanged; flanges drilled to
SANS 1123 Table 1600/3
| 3.01.03 | DN 600 Air Valve Chamber 2 as per
Drawing: JW14358-16941-T-013-S08-00-TMS
| 3.01.03.01 | Item 5: DN 100 PN16 Resilient Seal Gate Valve; Non manually operated; both ends flanged; flanges drilled to | No. | 1
rising spindle; anti-clockwise closing to SANS 664;
manually operated; both ends flanged; flanges drilled to
SANS 1123 Table 1600/3
| 3.01.03.02 | Item 6: DN 100 PN16 Double orifice with anti-shock orifice | No. | 1
mechanism air release valve, Vent-O-Mat RBX or similar
approved; flanges drilled to SANS 1123 Table 1600/3
| 3.01.03.03 | Item 7: DN 600 PN16 Wedge Gate Valve; Non rising | No. | 1
spindle; anti-clockwise closing to SANS 664; manually
operated; both ends flanged; flanges drilled
to SANS 1123 Table 1600/3
Carried forward
Part C - Section 2 - Air Valve Chambers: Nodes NA15,21,39,45,57,69,85,94,97, NC11
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 3.01.04 | DN 600 Air Valve Chamber 3 as per
Drawing: JW14358-16941-T-013-S10-00-TMS
| 3.01.04.01 | Item 5: DN 100 PN16 Resilient Seal Gate Valve; Non | No. | 1
rising spindle; anti-clockwise closing to SANS 664;
manually operated; both ends flanged; flanges drilled
to SANS 1123 Table 1600/3
| 3.01.04.02 | Item 6: DN 100 PN16 Double orifice with anti-shock orifice | No. | 1
mechanism air release valve, Vent-O-Mat RBX or similar
approved; flanges drilled to SANS 1123 Table 1600/3
| 3.01.04.03 | Item 7: DN 600 PN16 Wedge Gate Valve; Non rising to | No. | 1
spindle; anti-clockwise closing to SANS 664;
manually operated; both ends flanged; flanges drilled
SANS 1123 Table 1600/3
| 3.01.05 | DN 600 Air Valve Chamber 4 as per
Drawing: JW14358-16941-T-013-S13-00-TMS
| 3.01.05.01 | Item 5: DN 100 PN16 Resilient Seal Gate Valve; Non to | No. | 1
rising spindle; anti-clockwise closing to SANS 664;
manually operated; both ends flanged; flanges drilled
SANS 1123 Table 1600/3
| 3.01.05.02 | Item 6: DN 100 PN16 Double orifice with anti-shock orifice | No. | 1
mechanism air release valve, Vent-O-Mat RBX or similar
approved; flanges drilled to SANS 1123 Table 1600/3
| 3.01.05.03 | Item 7: DN 600 PN16 Wedge Gate Valve; Non rising | No. | 1
spindle; anti-clockwise closing to SANS 664; manually
operated; both ends flanged; flanges drilled to
SANS 1123 Table 1600/3
PSL 8.2.19 | 3.02 | Extra over PSL 8.2.1 or 8.2.16 for the Supplying,
Laying, Welding or Jointing and Bedding of
Steel specials
| 3.02.01 | DN 600 Air Valve Chamber 1 as per
Drawing: JW14358-16941-T-013-S04-00-TMS
| 3.02.01.01 | Item 1: Spool piece DN 600; wall thickness t = 6 mm | No. | 2
SANS 719; one end flanged to SANS 1123 Table 1600/3
| 3.02.01.02 | Item 2: Spool piece DN 600; wall thickness t = 6 mm | No. | 2
SANS 719; flanged both ends and drilled to
SANS 1123 Table 1600/3 with puddle flange
| 3.02.01.03 | Item 3: Unequal tee DN 600 x DN 400 mm SANS 719; | No. | 1
flanged all ends to SANS 1123 Table 1600/3;
With DN 600 pipe support
| 3.02.01.04 | Item 4: Spool piece DN 100 x 200 mm long; SANS 62 | No. | 1
heavy class; one end flanged DN 600 drilled to
SANS 1123 Table 1600/3; other end welded to DN 100
blank flange to SANS 1123 Table 1600/8 with holed
drilled for DN 100 pipe
Carried forward
Part C - Section 2 - Air Valve Chambers: Nodes NA15,21,39,45,57,69,85,94,97, NC11
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 3.02.02 | DN 200 Air Valve Chamber 2 as per
Drawing: JW14358-16941-T-013-S06-00-TMS
| 3.02.02.01 | Item 1: Spool piece DN 200; SANS 719 wall thickness | No. | 2
t = 6 mm; flanged both ends to SANS 1123 Table 1600/3
with puddle flange
| 3.02.02.02 | Item 2: Spool piece DN 200; wall thickness t = 6 mm | No. | 2
SANS 719; flanged both ends to SANS 1123 Table 1600/3
| 3.02.02.03 | Item 03: Unequal tee DN 200 x DN 100 mm SANS 719 | No. | 2
wall thickness t = 6 mm; Flanged all ends SANS 1123
Table 1600/3; With pipe support
| 3.02.02.04 | Item 4: Spool piece DN 100 x 250 mm long; SANS 62 | No. | 2
heavy class; both ends flanged, drilled to
SANS 1123 Table 1600/3
| 3.02.02.05 | Item 9: DN 250 Flange adaptor for High-Impact mPVC | No. | 2
Class 16 complete with shouldered end coupling system;
Flange drilled to SANS 1123 Table 1600/3
| 3.02.03 | DN 600 Air Valve Chamber 2 as per
Drawing: JW14358-16941-T-013-S08-00-TMS
| 3.02.03.01 | Item 1: Spool piece DN 600; wall thickness t = 6 mm | No. | 2
SANS 719; one end flanged to SANS 1123 Table 1600/3
| 3.02.03.02 | Item 2: Spool piece DN 600; wall thickness t = 6 mm | No. | 2
SANS 719; flanged both ends to SANS 1123 Table 1600/3
with puddle flange
| 3.02.03.03 | Item 3: Unequal tee DN 600 x DN 400 mm SANS 719; | No. | 1
flanged all ends to SANS 1123 Table 1600/3; With DN 600
pipe support
| 3.02.03.04 | Item 4: Spool piece DN 100, 200 mm long; SANS 62 | No. | 1
medium class; one end flanged DN 600 to SANS 1123
Table 1600/3; other end welded to DN 100 blank flange to
SANS 1123 Table 1600/8 with hole drilled for DN 100 pipe
| 3.02.04 | DN 600 Air Valve Chamber 3 as per
Drawing: JW14358-16941-T-013-S10-00-TMS
| 3.02.04.01 | Item 1: Spool piece DN 600; wall thickness t = 6 mm | No. | 2
SANS 719; one end flanged to SANS 1123 Table 1600/3
| 3.02.04.02 | Item 2: Spool piece DN 600; wall thickness t = 6 mm with | No. | 2
SANS 719; flanged both ends to SANS 1123 Table 1600/3
puddle flange
| 3.02.04.03 | Item 3: Unequal tee DN 600 x DN 400 mm SANS 719; | No. | 1
flanged all ends to SANS 1123 Table 1600/3; With DN 600
pipe support
Carried forward
Part C - Section 2 - Air Valve Chambers: Nodes NA15,21,39,45,57,69,85,94,97, NC11
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 3.02.04.04 | Item 4: Spool piece DN 100, 200 mm long; SANS 62 | No. | 1
medium class; one end flanged DN 600 to SANS 1123
Table 1600/3; other end welded to DN 100 blank flange to
SANS 1123 Table 1600/8 with hole drilled for DN 100 pipe
PSL 8.2.34 | 3.03 | Operation and Maintenance Manuals for Valves and
Flow Meters
| 3.03.01 | DN 100 Resilient Seal Gate Valve (PN16) | No. | 1
| 3.03.02 | DN 600 Wedge Gate Valve (PN16) | No. | 1
| 3.03.03 | DN 100 Air Valve (PN16) | No. | 1
Carried forward to summary (Part C - Section 2)
Part C - Section 2 - Air Valve Chambers: Nodes NA15,21,39,45,57,69,85,94,97, NC11
Concrete (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 2001 | 4 | CONCRETE (STRUCTURAL)
PART CC1
Refer to Drawing:
JW14358-16941-T-013-S03-00-TMS
SCHEDULED FORMWORK ITEMS
PSCC1.002 | 4.01 | Smooth:
| 4.01.01 | Vertical formwork to:
| 4.01.01.01 | Foundations (Floor) | m² | 60
| 4.01.01.02 | Plinths | m² | 12
| 4.01.01.03 | Walls | m² | 1060
| 4.01.01.04 | Sump | m² | 30
| 4.01.02 | Horizontal formwork to:
| 4.01.02.01 | Precast roof slabs | m² | 135
PSCC1.005 | 4.02 | Narrow widths (up to 300 mm wide):
| 4.02.01 | Vertical Smooth formwork to:
| 4.02.01.01 | Precast roof slabs | m | 300
PSCC1.006 | 4.03 | Box out holes/form voids:
| 4.03.01 | a) Small, circular, of diameter up to 0,35 m
| 4.03.01.01 | Over 0,5 m and up to and including 1,0 m | No. | 120
| 4.03.02 | d) Large, other than circular, areas over 0.1 m2 up
to 2,0 m2
| 4.03.02.01 | Over 0,5 m and up to and including 1,0 m | No. | 15
| 4.03.02.02 | Over 2,0 m deep | No. | 24
SCHEDULED REINFORCEMENT ITEMS
PSCC1.007 | 4.04 | Steel bars irrespective of grade and diameter
| 4.04.01 | a) Steel bars irrespective of grade and diameter | t | 57
Carried forward
Part C - Section 2 - Air Valve Chambers: Nodes NA15,21,39,45,57,69,85,94,97, NC11
Concrete (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
SCHEDULED CONCRETE ITEMS
PSCC1.011 | 4.05 | Blinding layer Grade 15 MPa/19 mm concrete
| 4.05.01 | 50 mm thickness | m² | 340
PSCC1.012 | 4.06 | Strength concrete
| 4.06.01 | Grade 30 MPa/19 mm concrete in
| 4.06.01.01 | Foundations (Floor) | m3 | 38
| 4.06.01.02 | Plinths | m3 | 8
| 4.06.01.03 | Walls | m3 | 130
| 4.06.01.04 | Roof | m3 | 29
| 4.06.01.05 | Sump | m3 | 11
PSCC1.013 | 4.07 | Unformed surface finishes
| 4.07.01 | a) Steel-floated finish
| 4.07.01.01 | Foundations (Floor) | m² | 73
| 4.07.01.02 | Top of Plinths | m² | 12
| 4.07.01.03 | Top of Walls | m² | 52
| 4.07.01.04 | Roof Slabs | m² | 114
| 4.07.02 | d) Broomed finish
| 4.07.02.01 | Blinding layer | m² | 355
| 4.07.03 | e) Screed in 3:1 Sand and Cement Mix
| 4.07.03.01 | Chamber floor screed | m3 | 20
PSCC1.015 | 4.08 | Joints
| 4.08.01 | Polysulphide sealant between precast slabs | m | 175
| 4.08.02 | Extruded butyl sealant between manhole rings | m | 35
PSCC1.015 | 4.08 | Joints
| 4.08.01 | Polysulphide sealant between precast slabs | m | 150
PSCC1.017 | 4.09 | Manufacture (or supply) and erect precast units:
| 4.09.01 | DN 1000 concrete ring manholes, 250 mm high, complete | No. | 10
with step irons
Carried forward
Part C - Section 2 - Air Valve Chambers: Nodes NA15,21,39,45,57,69,85,94,97, NC11
Concrete (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.018 | 4.10 | Grouting
| 4.10.01 | a) Under bases of pipe supports and straps | m³ | 12
| 4.10.02 | c) Pipe box-outs | m³ | 12
| 4.10.03 | d) Between precast sections and manhole rings | m³ | 2
PSCC1.019 | 4.11 | HD bolts and miscellaneous metal work
| 4.11.01 | Metal work for DN 600 Air Valve Chamber 1 as per
Drawing: JW14358-16941-T-013-S03-00-TMS
| 4.11.01.01 | Fabricate and install galvanised mild steel ladders as per | No. | 3
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.11.01.02 | Fabricate and cast in long inlet airvent as per | No. | 3
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.11.01.03 | Fabricate and cast in short outlet airvent as per | No. | 3
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.11.01.04 | Fabricate and cast in galvanised access manholes as per | No. | 3
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.11.01.05 | Fabricate and cast in lifting hooks as per bolt detail on | No. | 6
Drawing: JW14358-16941-T-017-S10-00-TMS
| 4.11.02 | Metal work for DN 600 Air Valve Chamber 2 as per
Drawing: JW14358-16941-T-013-S07-00-TMS
| 4.11.02.01 | Fabricate and install galvanised mild steel ladders as per | No. | 4
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.11.02.02 | Fabricate and cast in long inlet airvent as per | No. | 4
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.11.02.03 | Fabricate and cast in short outlet airvent as per | No. | 4
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.11.02.04 | Fabricate and cast in galvanised access manholes as per | No. | 4
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.11.02.05 | Fabricate and cast in lifting hooks as per bolt detail on | No. | 64
Drawing: JW14358-16941-T-017-S10-00-TMS
Carried forward
Part C - Section 2 - Air Valve Chambers: Nodes NA15,21,39,45,57,69,85,94,97, NC11
Concrete (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 4.11.03 | Metal work for DN 600 Air Valve Chamber 3 as per Drawing: JW14358-16941-T-013-S09-00-TMS
Drawing: JW14358-16941-T-013-S09-00-TMS
| 4.11.03.01 | Fabricate and install galvanised mild steel ladders as per Drawing: JW14358-16941-T-017-S09-00-TMS | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.11.03.02 | Fabricate and cast in long inlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.11.03.03 | Fabricate and cast in short outlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.11.03.04 | Fabricate and cast in galvanised access manholes as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.11.03.05 | Fabricate and cast in lifting hooks as per bolt detail on | No. | 16
Drawing: JW14358-16941-T-017-S10-00-TMS
| 4.11.04 | Metal work for DN 200 Air Valve Chamber as per
Drawing: JW14358-16941-T-013-S05-00-TMS
| 4.11.04.01 | Fabricate and install galvanised mild steel ladders as per Drawing: JW14358-16941-T-017-S09-00-TMS | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.11.04.02 | Fabricate and cast in long inlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.11.04.03 | Fabricate and cast in short outlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.11.04.04 | Fabricate and cast in galvanised access manholes as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.11.04.05 | Fabricate and cast in lifting hooks as per | No. | 12
Drawing: JW14358-16941-T-017-S10-00-TMS
PSCC1.020 | 4.12 | Colour Mitigation to:
| 4.12.01 | Exposed Chambers along roadways | m² | 144
MISCELLANEOUS ITEMS
PSCC1.021 | 4.13 | Polythene sheeting under concrete
| 4.13.01 | 250 micron green medium density polyethylene | m² | 355
dampproof sheeting
PSCC1.023 | 4.14 | FRP items
| 4.14.01 | c) FRP Grating
| 4.14.01.01 | 450 mm x 450 mm x 38 mm deep FRP grating as per | No. | 12
Drawing: JW14358-16941-T-013-S07-00-TMS
Carried forward
Part C - Section 2 - Air Valve Chambers: Nodes NA15,21,39,45,57,69,85,94,97, NC11
Concrete (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.024 | 4.14 | Casting pipes and specials in concrete
| 4.14.01 | DN 600 Steel pipe cast into chamber wall | No. | 22
| 4.14.02 | DN 200 Steel pipe cast into chamber wall | No. | 2
PSCC1.025 | 4.15 | Installation of precast elements
| 4.15.01 | Precast roof slabs as per | No. | 9
Drawing: JW14358-16941-T-013-S03-00-TMS
| 4.15.02 | Precast roof slabs as per | No. | 12
Drawing: JW14358-16941-T-013-S05-00-TMS
| 4.15.03 | Precast roof slabs as per | No. | 3
Drawing: JW14358-16941-T-013-S07-00-TMS
| 4.15.04 | Precast roof slabs as per | No. | 3
Drawing: JW14358-16941-T-013-S09-00-TMS
PSCC1.026 | 4.16 | Drilling cores through concrete
| 4.16.01 | 100 mm diameter core through 300 mm thick concrete | No. | 10
slab
Carried forward to summary (Part C - Section 2)
Part C - Section 2 - Air Valve Chambers: Nodes NA15,21,39,45,57,69,85,94,97, NC11
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SUMMARY
SANS 1200 C |  | SITE CLEARANCE
SANS 1200 DB |  | EARTHWORKS (PIPE TRENCHES)
SANS 1200 L |  | MEDIUM-PRESSURE PIPELINES
SANS 2001 CC1 |  | CONCRETE (STRUCTURAL)
Total carried forward to summary

## FM, SV-Chamber NC2 Part C
Part C - Section 3 - DN 200 Flow Meter and scour Valve Chamber: Node NC3
Site Clearance
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 C | 1 | SITE CLEARANCE
Refer to Drawing:
JW14358-16941-T-013-S23-00-TMS
PSC 8.2.1 | 1.01 | Clear and grub
| 1.01.01 | Areas | m² | 100
8.2.10 | 1.02 | Remove topsoil to nominal depth of 150 mm and | m³ | 15
stockpile
PSC 8.2.14 | 1.03 | Take down and re-erect existing fences and
guardrails
| 1.03.01 | a) Guardrails | m | 10
| 1.03.02 | b) Diamond mesh fencing | m | 10
Carried forward to summary (Part C - Section 3)
Part C - Section 3 - DN 200 Flow Meter and scour Valve Chamber: Node NC3
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 DB | 2 | EARTHWORKS (PIPE TRENCHES)
Refer to Drawing:
JW14358-16941-T-013-S23-00-TMS
PSDB 8.3.2 | 2.01 | Excavation
| 2.01.01 | d) Excavate in all materials for stormwater inlet and outlet structures and for manholes, catchpits, valve chambers and the like, irrespective of depth, and backfill around structures | m³ | 200
| 2.01.02 | e) Extra over 2.01.01 for excavating in
| 2.01.02.01 | 1) intermediate material | m³ | 20
| 2.01.02.02 | 2) hard material | m³ | 20
| 2.01.03 | f) Hand excavation where ordered by the Project Manager
| 2.01.03.01 | a) Soft material | m³ | 20
| 2.01.03.02 | b) Intermediate material | m³ | 20
| 2.01.03.03 | c) Hard material | m³ | 20
| 2.01.04 | g) Backfill stabilized with 5% cement where directed by the Project Manager | m³ | 40
| 2.01.05 | h) Soilcrete backfill where directed by the Project Manager | m³ | 40
Carried forward to summary (Part C - Section 3)
Part C - Section 3 - DN 200 Flow Meter and scour Valve Chamber: Node NC3
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 L | 3 | MEDIUM-PRESSURE PIPELINES
Refer to Drawing:
JW14358-16941-T-013-S24-00-TMS
8.2.3 | 3.01 | Extra-over PSL 8.2.1 for Supplying, Fixing, and
Bedding of Valves
| 3.01.01 | Item 6: DN 150 PN16 Resilient Seal Gate valve; non | No. | 3
rising spindle; anti-clockwise closing to SANS 664;
manually operated; both ends flanged; flanges drilled to
SANS 1123 Table 1600/3
| 3.01.02 | Item 13: DN 150 Single Door Swing Check Valve to | No. | 1
SANS 1551; Vosa or similar approved; flanged both ends
to SANS 1123 Table 1600/3
PSL 8.2.19 | 3.02 | Extra over 8.2.1 for the Supplying, Laying, Welding
or Jointing and Bedding of Steel specials
| 3.02.01 | Item 1: DN200 Flange adaptor for High-Impact mPVC | No. | 3
Class 16 complete with shouldered end coupling system;
flange drilled to SANS 1123 Table 1600/3
| 3.02.02 | Item 2: Concentric reducer DN 200 to DN 150; both ends | No. | 3
flanged; drilled to SANS 1123 Table 1600/3
| 3.02.03 | Item 3: Spool piece DN 150 x 1300 mm long; SANS 62 | No. | 2
Medium class; Flanged both ends; drilled to SANS 1123
Table 1600/3 with puddle flange
| 3.02.04 | Item 4: Equal Tee DN150 x DN150; SANS 62 Medium | No. | 1
class; all ends flanged; drilled to SANS 1123 Table 1600/3
| 3.02.05 | Item 5: Spool piece DN 150 x 506 mm long; SANS 62 | No. | 1
Medium class; Flanged both ends; drilled to SANS 1123
Table 1600/3; with pipe support
| 3.02.06 | Item 7: Spool piece DN 150 x 1300 mm long; SANS 62 | No. | 1
Medium class; Flanged both ends; drilled to SANS 1123
Table 1600/3; with puddle flange
| 3.02.07 | Item 8: Spool piece DN 150 x 300 mm long; SANS 62 | No. | 2
Medium class; Flanged both ends; drilled to SANS 1123
Table 1600/3
| 3.02.08 | Item 9a: DN150 Y-Strainer; Flanged both ends; drilled to | No. | 1
SANS 1123 Table 1600/3
| 3.02.09 | Item 9b: DN150 T-Strainer; Flanged both ends; drilled to | No. | 1
SANS 1123 Table 1600/3
| 3.02.10 | Item 10: Spool piece DN 150 x 750 mm long; SANS 62 | No. | 1
Medium class; Flanged both ends; drilled to SANS 1123
Table 1600/3; with pipe support
| 3.02.11 | Item 12: Spool piece DN 150 x 450 mm long; SANS 62 | No. | 1
Medium class; Flanged both ends; drilled to SANS 1123
Table 1600/3
Carried forward
Part C - Section 3 - DN 200 Flow Meter and scour Valve Chamber: Node NC3
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 3.02.12 | Item 14: Spool piece DN 150 x 300 mm long; SANS 62 | No. | 1
Medium class; Flanged both ends; drilled to SANS 1123
Table 1600/3; with pipe support
PSL 8.2.30 | 3.03 | Extra over 8.2.1 for for the Supplying, Installing and
Commissioning of Flow Meters
| 3.02.01 | Item 11: DN 150 PN16 Electromagnetic flow meter complete with sensor and remotely mounted transmitter; flanges drilled to SANS 1123 Table 1600/3; supplied with minimum 15 m of cable | No. | 1
PSL 8.2.34 | 3.04 | Operation and Maintenance Manuals for Valves and
Flow Meters
|  | DN150 Resilient Seal Gate Valve (PN16) | Sum | 1
|  | DN150 Electromagnetic Flow Meter (PN16) | Sum | 1
|  | DN150 Non-return Valve (PN16) | Sum | 1
Carried forward to summary (Part C - Section 3)
Part C - Section 3 - DN 200 Flow Meter and scour Valve Chamber: Node NC3
Cable ducts
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 LC | 4 | CABLE DUCTS
Refer to Drawings:
JW14358-16941-T-013-S23-00-TMS
JW14358-16941-T-013-S24-00-TMS
8.2.2 | 4.01 | Excavation
| 4.01.01 | a) Excavate in all materials for trenches, backfill, compact
and dispose of surplus material
| 4.01.01.01 | i) Single duct trench (300 mm wide), up to 1 m deep | m3 | 5
PSLC 8.2.5 | 4.02 | Supply, lay, bed and prove duct, including draw wire and
screening wire
|  | a) 110mm flexible conduit | m | 10
8.2.6 | 4.03 | Imported bedding material, where ordered
| 4.03.01 | a) Selected granular material | m3 | 3
Carried forward to summary (Part C - Section 3)
Part C - Section 3 - DN 200 Flow Meter and scour Valve Chamber: Node NC3
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 2001 | 5 | CONCRETE WORKS (STRUCTURAL)
PART CC1
Refer to Drawing:
JW14358-16941-T-013-S23-00-TMS
SCHEDULED FORMWORK ITEMS
PSCC1.002 | 5.01 | Smooth
| 5.01.01 | Vertical formwork to
| 5.01.01.01 | Foundations (Floor) | m² | 10
| 5.01.01.02 | Plinths | m² | 2
| 5.01.01.03 | Walls | m² | 150
| 5.01.01.04 | Sump | m² | 2
| 5.01.02 | Horizontal formwork to
| 5.01.02.01 | Precast roof slabs | m² | 20
PSCC1.005 | 5.02 | Narrow widths (up to 300 mm wide)
| 5.02.01 | Vertical Smooth formwork to
| 5.02.01.01 | Precast roof slabs | m | 50
| 5.02.01.02 | Concrete Bunker Apron Slab | m | 10
PSCC1.006 | 5.03 | Box out holes/form voids
| 5.03.01 | a) Small, circular, of diameter up to 0,35 m
| 5.03.01.01 | 0 m up to and including 0,5 m | No. | 20
| 5.03.02 | d) Large, other than circular, areas over 0.1 m2
up to 2,0 m2
| 5.03.02.01 | 0 m up to and including 0,5 m | No. | 1
| 5.03.02.02 | Over 2,0 m deep | No. | 3
SCHEDULED REINFORCEMENT ITEMS
PSCC1.007 | 5.04 | Steel bars
| 5.04.01 | (a) Steel bars irrespective of grade and diameter | t | 7
Carried forward
Part C - Section 3 - DN 200 Flow Meter and scour Valve Chamber: Node NC3
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
SCHEDULED CONCRETE ITEMS
PSCC1.011 | 5.05 | Blinding layer in Grade 15 MPa/19 mm concrete
| 5.05.01 | 50 mm thickness | m² | 45
PSCC1.012 | 5.06 | Strength concrete
| 5.06.01 | Class 30 MPa/19 mm concrete in
| 5.06.01.01 | Foundations (Floor) | m3 | 6
| 5.06.01.02 | Plinths | m3 | 1
| 5.06.01.03 | Walls | m3 | 17
| 5.06.01.04 | Roof Slabs | m3 | 4
| 5.06.01.05 | Sump | m3 | 1
| 5.06.01.06 | Concrete Bunker Apron Slab | m3 | 1
PSCC1.013 | 5.07 | Unformed surface finishes
| 5.07.01 | a) Steel-floated finish
| 5.07.01.01 | Foundations (Floor) | m² | 15
| 5.07.01.02 | Top of Plinths | m² | 2
| 5.07.01.03 | Top of Walls | m² | 10
| 5.07.01.04 | Roof Slabs | m² | 16
| 5.07.01.05 | Concrete Bunker Apron Slab | m² | 10
| 5.08.02 | d) Broomed finish
| 5.08.02.01 | Blinding layer | m² | 45
| 5.08.03 | e) Screed in 3:1 Sand and Cement Mix
| 5.08.03.01 | Chamber floor screed | m³ | 2
PSCC1.016 | 5.08 | Joints
| 5.08.01 | Polysulphide sealant between precast slabs | m | 35
PSCC1.017 | 5.09 | Manufacture (or supply) and erect precast units
| 5.09.01 | Concrete Bunker (Minimum Internal Dimesions: | No. | 1
680 H x 500 W x 375 D)
Carried forward
Part C - Section 3 - DN 200 Flow Meter and scour Valve Chamber: Node NC3
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.018 | 5.10 | Grouting
| 5.10.01 | a) Under bases of pipe supports and straps | m³ | 1
| 5.10.02 | c) Pipe box-outs | m³ | 1
PSCC1.019 | 5.11 | HD bolts and miscellaneous metal work
| 5.11.01 | Metal work for DN 200 Flow Meter and Scour Valve
Chamber as per
Drawing: JW14358-16941-T-013-S23-00-TMS
| 5.11.01.01 | Fabricate and install galvanised mild steel ladders as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.01.02 | Fabricate and cast in long inlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.01.03 | Fabricate and cast in short outlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.01.04 | Fabricate and cast in galvanised access manholes as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.01.05 | Fabricate and cast in lifting hooks as per bolt detail on | No. | 20
Drawing: JW14358-16941-T-017-S10-00-TMS
| 5.11.01.06 | Fabricate and install DN 160 galvanised medium duty pipe | No. | 3
clamps as per
Drawing: JW14358-16941-T-017-S10-00-TMS
PSCC1.020 | 5.12 | Colour Mitigation to
| 5.12.01 | Exposed Chambers along roadways | m² | 15
MISCELLANEOUS ITEMS
PSCC1.021 | 5.13 | Polythene sheeting under concrete
| 5.13.01 | 250 micron green medium density polyethylene | m² | 45
dampproof sheeting
PSCC1.023 | 5.14 | FRP items
| 5.14.01 | c) FRP Grating
| 5.14.01.01 | 450 mm x 450 mm x 38 mm deep FRP grating as per | No. | 1
Drawing: JW14358-16941-T-013-S23-00-TMS
PSCC1.024 | 5.15 | Casting pipes and specials in concrete
| 5.15.01 | DN 150 Steel pipe cast into chamber wall | No. | 3
Carried forward
Part C - Section 3 - DN 200 Flow Meter and scour Valve Chamber: Node NC3
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.025 | 5.16 | Installation of precast elements
| 5.16.01 | Precast roof slabs as per | No. | 5
Drawing: JW14358-16941-T-013-S23-00-TMS
PSCC1.026 | 5.17 | Drilling cores through concrete
| 5.17.01 | 100 mm diameter core through 250 mm thick | No. | 3
concrete slab
Carried forward to summary (Part C - Section 3)
Part C - Section 3 - DN 200 Flow Meter and scour Valve Chamber: Node NC3
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SUMMARY
SANS 1200 C |  | SITE CLEARANCE
SANS 1200 DB |  | EARTHWORKS (PIPE TRENCHES)
SANS 1200 L |  | MEDIUM-PRESSURE PIPELINES
SANS 1200 LC |  | CABLE DUCTS
SANS 2001 CC1 |  | CONCRETE WORKS (STRUCTURAL)
Total carried forward to summary

## IV, SV-Chamber ND2 Part C
Part C - Section 4 - DN 800 isolation, scour and future tie-in chamber: Node ND2
Site Clearance
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 C | 1 | SITE CLEARANCE
Refer to Drawing:
JW14358-16941-T-013-S53-00-TMS
PSC 8.2.1 | 1.01 | Clear and grub
| 1.01.01 | Areas | m² | 140
8.2.2 | 1.02 | Remove and grub large trees and tree stumps
of girth
| 1.02.01 | Over 1 m and up to and including 2 m | No. | 1
8.2.10 | 1.03 | Remove topsoil to nominal depth of 150 mm and stockpile | m³ | 21
PSC 8.2.14 | 1.04 | Take down and re-erect existing fences and
guardrails
| 1.04.01 | a) Guardrails | m | 10
| 1.04.02 | b) Diamond mesh fencing | m | 10
Carried forward to summary (Part C - Section 4)
Part C - Section 4 - DN 800 isolation, scour and future tie-in chamber: Node ND2
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 DB | 2 | EARTHWORKS (PIPE TRENCHES)
Refer to Drawing:
JW14358-16941-T-013-S53-00-TMS
| 2.01 | Excavation
PSDB 8.3.2
| 2.01.01 | d) Excavate in all materials for stormwater inlet and outlet | m³ | 360
structures and for manholes, catchpits, valve chambers
and the like, irrespective of depth, and backfill around
structures
| 2.01.02 | e) Extra over 2.01.01 for excavating in
| 2.01.02.01 | 1) intermediate material | m³ | 40
| 2.01.02.02 | 2) hard material | m³ | 40
| 2.01.03 | f) Hand excavation where ordered by the
Project Manager
| 2.01.03.01 | a) Soft material | m³ | 40
| 2.01.03.02 | b) Intermediate material | m³ | 40
| 2.01.03.03 | c) Hard material | m³ | 40
| 2.01.04 | g) Backfill stabilized with 5% cement where directed by | m³ | 80
the Project Manager
| 2.01.05 | h) Soilcrete backfill where directed by the Project Manager | m³ | 80
Carried forward to summary (Part C - Section 4)
Part C - Section 4 - DN 800 isolation, scour and future tie-in chamber: Node ND2
Gabions and pitching
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 DK | 3 | GABIONS AND PITCHING
Refer to Drawing: JW14358-16941-T-013-S53-00-TMS
JW14358-16941-T-013-S53-00-TMS
8.2.2 | 3.01 | Gabions
| 3.01.01 | Gabion mattresses of galvanized wire, up to 0,3 m
deep
| 3.01.01.01 | 60 mm x 80 mm mesh, 2.2 mm dia wire, | m³ | 5
6 m x 2 m x 0.17 m mattress
8.2.4 | 3.02 | Geotextile
| 3.02.01 | Bidim A4 or approved equivalent | m² | 50
8.2.5 | 3.03 | Pitching
| 3.03.01 | Grouted pitching
| 3.03.01.01 | a) Light pitching | m³ | 15
Carried forward to summary (Part C - Section 4)
Part C - Section 4 - DN 800 isolation, scour and future tie-in chamber: Node ND2
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 L | 4 | MEDIUM-PRESSURE PIPELINES
Refer to Drawing:
JW14358-16941-T-13-S54-0-TMS
8.2.3 | 4.01 | Extra-over PSL 8.2.16 for Supplying, Fixing, and
Bedding of Valves
| 4.01.01 | Item 2: DN 800 PN25 wedge gate valve for vertical | No. | 2
operation; non rising spindle; anti-clockwise closing to
SANS 664; manually operated; Vosa or similar approved;
both ends flanged; drilled to SANS 1123 Table 2500/3
| 4.01.02 | Item 10: DN 250 PN25 wedge gate valve for vertical | No. | 3
operation; non rising spindle; anti-clockwise closing to
SANS 664; manually operated; Vosa or similar approved;
both ends flanged; drilled to SANS 1123 Table 2500/3
PSL 8.2.19 | 4.02 | Extra over 8.2.16 for the Supplying, Laying, Welding
or Jointing and Bedding of Steel specials
| 4.02.01 | Item 1: Spool piece DN 800 x 1400 mm long SANS 719; | No. | 3
Wall thickness t = 8 mm; flanged both ends; drilled to
SANS 1123 Table 2500/3; with puddle flange
| 4.02.02 | Item 3: Unequal Tee DN 800 x 8 mm x DN 250 x 6 mm; | No. | 5
SANS719; flanged both ends; drilled to
SANS 1123 Table 2500/3
| 4.02.03 | Item 4: Equal tee; DN 800 x DN 800; SANS 719; | No. | 1
Wall thickness t = 8 mm; all ends flanged; drilled to
SANS 1123 Table 2500/3
| 4.02.04 | Item 5: Spool piece DN 800 SANS 719; 1500 mm long; | No. | 1
Wall thickness t = 8 mm; flanged both ends to; drilled
SANS 1123 Table 2500/3; with puddle flange
| 4.02.05 | Item 6: Blank flange DN 800; drilled to | No. | 1
SANS 1123 Table 2500/8
| 4.02.06 | Item 7: Spool piece DN 800 SANS 719; 500 mm long; | No. | 2
Wall thickness t = 8 mm; one end flanged; drilled to
SANS 1123 Table 2500/3
| 4.02.07 | Item 8: 90 Degree 3 segment short radius bend; DN 250; | No. | 4
SANS 719; Wall thickness t = 6 mm wall; flanged both
ends; drilled toSANS 1123 Table 2500/3
| 4.02.08 | Item 9: Spool piece DN 250 457 mm long; SANS 719; to | No. | 4
Wall thickness t= 6 mm; flanged both ends; drilled to
SANS 1123 Table 2500/3
| 4.02.09 | Item 11: Spool piece DN 250 x 1000 mm long; | No. | 1
Wall thickness t = 6 mm; one end flanged; drilled
to SANS 1123 Table 2500/3
Carried forward
Part C - Section 4 - DN 800 isolation, scour and future tie-in chamber: Node ND2
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSL 8.2.34 | 4.03 | Operation and Maintenance Manuals for Valves and
Flow Meters
|  | DN250 Wedge Gate Valve (PN25) | Sum | 1
|  | DN800 Wedge Gate Valve (PN25) | Sum | 1
Carried forward to summary (Part C - Section 4)
Part C - Section 4 - DN 800 isolation, scour and future tie-in chamber: Node ND2
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 2001 | 5 | CONCRETE WORKS (STRUCTURAL)
PART CC1
Refer to Drawing:
JW14358-16941-T-013-S53-00-TMS
SCHEDULED FORMWORK ITEMS
PSCC1.002 | 5.01 | Smooth
| 5.01.01 | Vertical formwork to
| 5.01.01.01 | Foundations (Floor) | m² | 8
| 5.01.01.02 | Plinths | m² | 2
| 5.01.01.03 | Walls | m² | 220
| 5.01.01.04 | Sump | m² | 2
| 5.01.02 | Horizontal formwork to
| 5.01.02.01 | Slabs | m² | 45
PSCC1.005 | 5.02 | Narrow widths (up to 300 mm wide)
| 5.02.01 | Vertical Smooth formwork to
| 5.02.01.01 | Precast roof slabs | m | 120
PSCC1.006 | 5.03 | Box out holes/form voids
| 5.03.01 | a) Small, circular, of diameter up to 0,35 m
| 5.03.01.01 | 0 m up to and including 0,5 m | No. | 40
| 5.03.02 | d) Large, other than circular, areas over 0.1 m2 up
to 2,0 m2
| 5.03.02.01 | 0 m up to and including 0,5 m | No. | 2
| 5.03.02.02 | Over 2,0 m deep | No. | 4
SCHEDULED REINFORCEMENT ITEMS
PSCC1.007 | 5.04 | Steel bars
| 5.04.01 | a) Steel bars irrespective of grade and diameter | t | 21
Carried forward
Part C - Section 4 - DN 800 isolation, scour and future tie-in chamber: Node ND2
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
SCHEDULED CONCRETE ITEMS
PSCC1.011 | 5.05 | Blinding layer in Grade 15 MPa/19 mm concrete
| 5.05.01 | 50 mm thickness | m² | 85
PSCC1.012 | 5.06 | Strength concrete
| 5.06.01 | Class 30 MPa/19 mm concrete in
| 5.06.01.01 | Foundations (Floor) | m3 | 20
| 5.06.01.02 | Plinths | m3 | 2
| 5.06.01.03 | Walls | m3 | 58
| 5.06.01.04 | Roof slab | m3 | 12
| 5.06.01.05 | Sump | m3 | 2
PSCC1.013 | 5.07 | Unformed surface finishes
| 5.07.01 | a) Steel-floated finish
| 5.07.01.01 | Foundations (Floor) | m² | 30
| 5.07.01.02 | Top of Plinths | m² | 2
| 5.07.01.03 | Top of Walls | m² | 30
| 5.07.01.04 | Roof Slabs | m² | 48
| 5.07.02 | d) Broomed finish
| 5.07.02.01 | Blinding layer | m² | 85
| 5.08.03 | e) Screed in 3:1 Sand and Cement Mix
| 5.08.03.01 | Chamber floor screed | m³ | 5
PSCC1.016 | 5.08 | Joints
| 5.08.01 | Polysulphide sealant between precast slabs | m | 65
PSCC1.018 | 5.09 | Grouting
| 5.09.01 | a) Under bases of pipe supports and straps | m³ | 1
| 5.09.02 | c) Pipe box-outs | m³ | 2
Carried forward
Part C - Section 4 - DN 800 isolation, scour and future tie-in chamber: Node ND2
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.019 | 5.10 | HD bolts and miscellaneous metal work
| 5.10.01 | Metal work for DN 800 Isolation, scour and future tie-in
Chamber as per
Drawing: JW14358-16941-T-013-S53-00-TMS
| 5.10.01.01 | Fabricate and install galvanised mild steel ladders as per | No. | 2
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.10.01.02 | Fabricate and cast in long inlet airvent as per | No. | 2
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.10.01.03 | Fabricate and cast in short outlet airvent as per | No. | 2
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.10.01.04 | Fabricate and cast in galvanised access manholes as per | No. | 2
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.10.01.05 | Fabricate and cast in galvanised overflow frame a | No. | 1
nd grating as per
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.10.01.06 | Fabricate and cast in lifting hooks as per bolt detail on | No. | 40
Drawing: JW14358-16941-T-017-S10-00-TMS
| 5.10.01.07 | Fabricate and install galvanised steel grating platform, | t | 0.5
including frame and supports
| 5.10.01.08 | Fabricate and install galvanised steel handrails | t | 0.2
PSCC1.020 | 5.11 | Colour Mitigation to
| 5.11.01 | Exposed Chambers along roadways | m² | 30
MISCELLANEOUS ITEMS
PSCC1.021 | 5.12 | Polythene sheeting under concrete
| 5.12.01 | 250 micron green medium density polyethylene d | m² | 85
ampproof sheeting
PSCC1.023 | 5.13 | FRP items
| 5.13.01 | b) FRP Handrails
| 5.13.01.01 | Round hand railing system | m | 18
| 5.13.02 | c) FRP Grating
| 5.13.02.01 | 450 mm x 450 mm x 38 mm deep FRP grating | No. | 3
| 5.13.03 | e) FRP platforms including frames and supports
| 5.13.03.01 | 38 mm deep FRP grating platform | m² | 15
Carried forward
Part C - Section 4 - DN 800 isolation, scour and future tie-in chamber: Node ND2
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.024 | 5.14 | Casting pipes and specials in concrete
| 5.14.01 | DN 250 Steel pipe cast into chamber wall | No. | 1
| 5.14.02 | DN 800 Steel pipe cast into chamber wall | No. | 3
PSCC1.025 | 5.15 | Installation of precast elements
| 5.15.01 | Precast roof slabs as per | No. | 10
Drawing: JW14358-16941-T-013-S53-00-TMS
PSCC1.026 | 5.16 | Drilling cores through concrete
| 5.16.01 | 100 mm diameter core through 250 mm thick concrete | No. | 3
slab
Carried forward to summary (Part C - Section 4)
Part C - Section 4 - DN 800 isolation, scour and future tie-in chamber: Node ND2
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SUMMARY
SANS 1200 C |  | SITE CLEARANCE
SANS 1200 DB |  | EARTHWORKS (PIPE TRENCHES)
SANS 1200 DK |  | GABIONS AND PITCHING
SANS 1200 L |  | MEDIUM-PRESSURE PIPELINES
SANS 2001 CC1 |  | CONCRETE WORKS (STRUCTURAL)
Total carried forward to summary

## Hot Tapping Chambers
Part C - Section 5 - Hot-Tapping chambers: Node NA1, ND1, ND5
Site Clearance
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 C | 1 | SITE CLEARANCE
Refer to Drawings: , ,
JW14358-16941-T-013-S30-00-TMS
JW13038-16941-T-013-S32-00-TMS
JW14358-16941-T-013-S51-00-TMS
PSC 8.2.1 | 1.01 | Clear and grub
| 1.01.01 | Areas | m² | 300
8.2.2 | 1.02 | Remove and grub large trees and tree stumps of
girth
| 1.02.01 | Over 1 m and up to and including 2 m | No. | 4
8.2.10 | 1.03 | Remove topsoil to nominal depth of 150 mm and stockpile | m³ | 45
PSC 8.2.14 | 1.04 | Take down and re-erect existing fences and
guardrails
| 1.04.01 | a) Guardrails | m | 15
| 1.04.02 | b) Diamond mesh fencing | m | 15
Carried forward to summary (Part C - Section 5)
Part C - Section 5 - Hot-Tapping chambers: Node NA1, ND1, ND5
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 DB | 2 | EARTHWORKS (PIPE TRENCHES)
Refer to Drawings: JW14358-16941-T-013-S30-00-TMS, JW13038-16941-T-013-S32-00-TMS, JW14358-16941-T-013-S51-00-TMS
JW14358-16941-T-013-S30-00-TMS
JW13038-16941-T-013-S32-00-TMS
JW14358-16941-T-013-S51-00-TMS
PSDB 8.3.2 | 2.01 | Excavation
| 2.01.01 | d) Excavate in all materials for stormwater inlet and outlet | m³ | 750
structures and for manholes, catchpits, valve chambers
and the like, irrespective of depth, and backfill around
structures
| 2.01.02 | e) Extra over 2.01.01 for excavating in
| 2.01.02.01 | 1) intermediate material | m³ | 75
| 2.01.02.02 | 2) hard material | m³ | 75
| 2.01.03 | f) Hand excavation where ordered by the Project Manager
| 2.01.03.01 | a) Soft material | m³ | 75
| 2.01.03.02 | b) Intermediate material | m³ | 75
| 2.01.03.03 | c) Hard material | m³ | 75
| 2.01.04 | g) Backfill stabilized with 5% cement where directed by | m³ | 150
the Project Manager
| 2.01.05 | h) Soilcrete backfill where directed by the Project Manager | m³ | 150
Carried forward to summary (Part C - Section 5)
Part C - Section 5 - Hot-Tapping chambers: Node NA1, ND1, ND5
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 L | 3 | MEDIUM-PRESSURE PIPELINES
8.2.3 | 3.01 | Extra-over PSL 8.2.16 for Supplying, Fixing, and
Bedding of Valves
| 3.01.01 | DN 525 Tie-in Chamber as per
Drawing: JW14358-16941-T-013-S31-00-TMS
| 3.01.01.01 | Item 3: DN 500 PN25 wedge gate valve for vertical | No. | 1
operation; non rising spindle; anti-clockwise closing to
SANS 664; manually operated; Vosa or similar
approved; both ends flanged; flanges drilled to
SANS 1123 Table 2500/3
| 3.01.01.02 | Item 7: DN 250 PN25 wedge gate valve for vertical | No. | 1
operation; non rising spindle; anti-clockwise closing to
SANS 664; manually operated; Vosa or similar
approved; both ends flanged; flanges drilled to
SANS 1123 Table 2500/3
| 3.01.02 | DN 600 to DN 1500 Tie-in Chamber as per
Drawing: JW14358-16941-T-013-S33-00-TMS
| 3.01.02.01 | Item 3: DN 600 PN25 wedge gate valve for vertical | No. | 1
operation; non rising spindle; anti-clockwise closing to
SANS 664; manually operated; Vosa or similar
approved; both ends flanged; flanges drilled to
SANS 1123 Table 2500/3
| 3.01.02.02 | Item 7: DN 250 PN25 wedge gate valve for vertical | No. | 1
operation; non rising spindle; anti-clockwise closing to
SANS 664; manually operated; Vosa or similar
approved; both ends flanged; flanges drilled to
SANS 1123 Table 2500/3
| 3.01.03 | DN 800 Tie-in Chamber as per
Drawing: JW14358-16941-T-013-S52-00-TMS
| 3.01.03.01 | Item 3: DN 800 PN25 wedge gate valve for vertical | No. | 1
operation; non rising spindle; anti-clockwise closing to
SANS 664; manually operated; Vosa or similar
approved; both ends flanged; flanges drilled to
SANS 1123 Table 2500/3
| 3.01.03.02 | Item 7: DN 250 PN25 wedge gate valve for vertical | No. | 1
operation; non rising spindle; anti-clockwise closing to
SANS 664; manually operated; Vosa or similar
approved; both ends flanged; flanges drilled to
SANS 1123 Table 2500/3
PSL 8.2.19 | 3.02 | Extra over 8.2.16 for the Supplying, Laying, Welding
or Jointing and Bedding of Steel specials
| 3.02.01 | DN 525 Tie-in Chamber as per
Drawing: JW14358-16941-T-013-S31-00-TMS
| 3.02.01.01 | Item 1: Spool piece DN 800 x 500 mm long; SANS 719; | No. | 1
wall thickness t = 8 mm; flanged one end; drilled to
SANS 1123 Table 2500/3
Carried forward
Part C - Section 5 - Hot-Tapping chambers: Node NA1, ND1, ND5
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 3.02.01.02 | Item 2: Spool piece DN 800 x 1290 mm long; SANS 719; | No. | 1
wall thickness t = 8 mm; flanged both ends; drilled to
SANS 1123 Table 2500/3; with puddle flange
| 3.02.01.03 | Item 5: Unequal Tee DN 500 x DN 250; SANS 719; | No. | 2
wall thickness t = 6 mm; all ends flanged; drilled to
SANS 1123 Table 2500/3
| 3.02.01.04 | Item 6: Spool piece DN 250 x 307 mm long; SANS 719; | No. | 2
wall thickess t = 6 mm; flanged both ends; drilled to
SANS 1123 Table 2500/3
| 3.02.01.05 | Item 8: 3 Segment Short Radius Bend 90 ̊, DN 250 | No. | 2
wall thickness t = 6 mm SANS 719; R=280, Both ends
flanged; drilled to SANS 1123 Table 2500/3
| 3.02.01.06 | Item 9: Concentric reducer DN 800 x DN 500 x 600 mm | No. | 1
long; SANS 719; wall thickness t = 8 mm; flanged both
ends; drilled to SANS 1123 Table 2500/3
| 3.02.02 | DN 600 to DN 1500 Tie-in Chamber as per
Drawing: JW14358-16941-T-013-S33-00-TMS
| 3.02.02.01 | Item 1: Spool piece DN 600 x 500 mm long; SANS 719; | No. | 1
wall thickess t = 6 mm; flanged one end; drilled to
SANS 1123 Table 2500/3
| 3.02.02.02 | Item 2: Spool piece DN 600 x 964 mm long; SANS 719; | No. | 1
wall thickness t = 6 mm; flanged both ends; drilled to
SANS 1123 Table 2500/3; with puddle flange
| 3.02.02.03 | Item 5: Unequal Tee DN 600 x DN 250; SANS 719; | No. | 2
wall thickness t = 6 mm; all ends flanged; drilled to
SANS 1123 Table 2500/3
| 3.02.02.04 | Item 6: Spool piece DN 600 x 452 mm long; SANS 719; | No. | 2
wall thickness t = 6 mm; flanged both ends; drilled to
SANS 1123 Table 2500/3
| 3.02.02.05 | Item 8: 90 Degree 3 segment short radius bend; DN 250; | No. | 2
SANS 719; wall thickness t = 6 mm; flanged both ends;
drilled to SANS 1123 Table 2500/3
| 3.02.03 | DN 800 Tie-in Chamber as per
Drawing: JW14358-16941-T-013-S52-00-TMS
| 3.02.03.01 | Item 1: Spool piece DN 800 x 500 mm long; SANS 719; | No. | 1
wall thickess t = 8 mm; flanged one end; drilled to
SANS 1123 Table 2500/3
| 3.02.03.02 | Item 2: Spool piece DN 800 x 1464 mm long; SANS 719; | No. | 1
wall thickness t = 8 mm; flanged both ends; drilled to
SANS 1123 Table 2500/3; with puddle flange
| 3.02.03.03 | Item 5: Unequal Tee DN 800 wall thickess t = 8 mm x all | No. | 2
DN 250 wall thickness t = 6 mm; SANS 719; all ends
flanged; drilled to SANS 1123 Table 2500/3
Carried forward
Part C - Section 5 - Hot-Tapping chambers: Node NA1, ND1, ND5
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 3.02.03.04 | Item 6: Spool piece DN 250 x 730 mm long; SANS 719; | No. | 2
wall thickess t = 6 mm; flanged both ends; drilled to
SANS 1123 Table 2500/3
| 3.02.03.05 | Item 8: 90 Degree 3 segment short radius bend; DN 250; | No. | 2
SANS 719; wall thickness t = 6 mm; flanged both ends;
drilled to SANS 1123 Table 2500/3
PSL 8.2.28 | 3.03 | Connect to Existing Mains using Hot Tapping
| 3.03.01 | a) Connect DN 600 (PN25) stub to existing DN 1500 | No. | 1
pipeline
| 3.03.02 | b) Connect DN 800 (PN25) stub to existing DN 1200 | No. | 1
pipeline
| 3.03.03 | c) Connect DN 500 (PN25) stub to existing DN 525 | No. | 1
pipeline
PSL 8.2.34 | 3.04 | Operation and Maintenance Manuals for Valves and Flow Meters
| 3.05.01 | DN 500 Wedge Gate Valve (PN25) | Sum | 1
| 3.05.02 | DN 600 Wedge Gate Valve (PN25) | Sum | 1
| 3.05.03 | DN 800 Wedge Gate Valve (PN25) | Sum | 1
Carried forward to summary (Part C - Section 5)
Part C - Section 5 - Hot-Tapping chambers: Node NA1, ND1, ND5
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 2001 | 4 | CONCRETE WORKS (STRUCTURAL)
PART CC1
Refer to Drawings: JW14358-16941-T-013-S30-00-TMS, JW13038-16941-T-013-S32-00-TMS, JW14358-16941-T-013-S51-00-TMS
JW14358-16941-T-013-S30-00-TMS
JW13038-16941-T-013-S32-00-TMS
JW14358-16941-T-013-S51-00-TMS
SCHEDULED FORMWORK ITEMS
PSCC1.002 | 4.01 | Smooth
| 4.01.01 | Vertical formwork to
| 4.01.01.01 | Foundations (Floor) | m² | 20
| 4.01.01.02 | Plinths | m² | 10
| 4.01.01.03 | Walls | m² | 500
| 4.01.01.04 | Sump | m² | 3
| 4.01.01.05 | Stairs | m² | 32
| 4.01.02 | Horizontal formwork to
| 4.01.02.01 | Slabs | m² | 75
PSCC1.005 | 4.02 | Narrow widths (up to 300 mm wide)
| 4.02.01 | Vertical Smooth formwork to
| 4.02.01.01 | Precast slabs | m | 200
PSCC1.006 | 4.03 | Box out holes/form voids
| 4.03.01 | a) Small, circular, of diameter up to 0,35 m
| 4.03.01.01 | 0 m up to and including 0,5 m | No. | 52
| 4.03.02 | d) Large, other than circular, areas over 0.1 m2
up to 2,0 m2
| 4.03.02.01 | 0 m up to and including 0,5 m | No. | 3
| 4.03.02.02 | Over 2,0 m deep | No. | 9
SCHEDULED REINFORCEMENT ITEMS
PSCC1.007 | 4.04 | Steel bars
| 4.04.01 | a) Steel bars irrespective of grade and diameter | t | 30
SCHEDULED CONCRETE ITEMS
PSCC1.011 | 4.05 | Blinding layer in Grade 15 MPa/19 mm concrete
| 4.05.01 | 50 mm thickness | m² | 165
Carried forward
Part C - Section 5 - Hot-Tapping chambers: Node NA1, ND1, ND5
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.012 | 4.06 | Strength concrete
| 4.06.01 | Class 30 MPa/19 mm concrete in: |  |  |  |  | `
| 4.06.01.01 | Foundations (Floor) | m3 | 20
| 4.06.01.02 | Plinths | m3 | 6
| 4.06.01.03 | Walls | m3 | 70
| 4.06.01.04 | Roof slab | m3 | 20
| 4.06.01.05 | Sump | m3 | 4
| 4.06.01.06 | Stairs | m3 | 8
PSCC1.013 | 4.07 | Unformed surface finishes
| 4.07.01 | a) Steel-floated finish
| 4.07.01.01 | Foundations (Floor) | m² | 80
| 4.07.01.02 | Top of Plinths | m² | 4
| 4.07.01.03 | Top of Walls | m² | 30
| 4.07.02 | d) Broomed finish
| 4.07.02.01 | Blinding layer | m² | 165
| 4.07.03 | e) Screed in 3:1 Sand and Cement Mix
| 4.07.03.01 | Chamber floor screed | m³ | 8
PSCC1.015 | 4.08 | Joints
| 4.08.01 | Polysulphide sealant between precast slab | m | 80
PSCC1.018 | 4.09 | Grouting
| 4.09.01 | a) Under bases of pipe supports and straps | m³ | 4
| 4.09.02 | b) Pipe box-outs | m³ | 4
PSCC1.019 | 4.10 | HD bolts and miscellaneous metal work
| 4.10.01 | DN 525 Tie-in Chamber as per Drawings:
JW14358-16941-T-013-S30-00-TMS
JW14358-16941-T-013-S31-00-TMS
| 4.10.01.01 | Fabricate and install galvanised mild steel ladders as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.10.01.02 | Fabricate and cast in long inlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
Carried forward
Part C - Section 5 - Hot-Tapping chambers: Node NA1, ND1, ND5
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 4.10.01.03 | Fabricate and cast in short outlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.10.01.04 | Fabricate and cast in galvanised access manholes as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.10.01.05 | Fabricate and cast in lifting hooks as per bolt detail on | No. | 16
Drawing:JW14358-16941-T-017-S10-00-TMS
| 4.10.01.06 | Fabricate and install galvanised steel grating platform, | t | 0.5
including frame and supports
| 4.10.01.07 | Fabricate and install galvanised steel handrails | t | 0.2
| 4.10.02 | DN 600 to DN 1500 Tie-in Chamber as per Drawings:
JW14358-16941-T-013-S32-00-TMS
JW14358-16941-T-013-S33-00-TMS
| 4.10.02.01 | Fabricate and install galvanised mild steel ladders as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.10.02.02 | Fabricate and cast in long inlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.10.02.03 | Fabricate and cast in short outlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.10.02.04 | Fabricate and cast in galvanised access manholes as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.10.02.05 | Fabricate and cast in lifting hooks as per bolt detail on | No. | 16
Drawing: JW14358-16941-T-017-S10-00-TMS
| 4.10.02.06 | Fabricate and install galvanised steel grating platform, | t | 0.5
including frame and supports
| 4.10.02.07 | Fabricate and install galvanised steel handrails | t | 0.2
| 4.10.03 | DN 800 Tie-in Chamber as per Drawing:
JW14358-16941-T-013-S51-00-TMS
JW14358-16941-T-013-S52-00-TMS
| 4.10.03.01 | Fabricate and install galvanised mild steel ladders as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.10.03.02 | Fabricate and cast in long inlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.10.03.03 | Fabricate and cast in short outlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.10.03.04 | Fabricate and cast in galvanised access manholes as per drawing JW14358-16941-T-017-S09-00-TMS | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.10.03.05 | Fabricate and cast in lifting hooks as per bolt detail on drawing JW14358-16941-T-017-S10-00-TMS | No. | 20
Drawing: JW14358-16941-T-017-S10-00-TMS
Carried forward
Part C - Section 5 - Hot-Tapping chambers: Node NA1, ND1, ND5
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 4.10.03.06 | Fabricate and install galvanised steel grating platform, | t | 0.5
including frame and supports
| 4.10.03.07 | Fabricate and install galvanised steel handrails | t | 0.2
PSCC1.020 | 4.11 | Colour Mitigation to
| 4.11.01 | Exposed Chambers along roadways | m² | 190
MISCELLANEOUS ITEMS
PSCC1.021 | 4.12 | Polythene sheeting under concrete
| 4.12.01 | 250 micron green medium density polyethylene | m² | 165
dampproof sheeting
PSCC1.023 | 4.13 | FRP items
| 4.13.01 | b) FRP Handrails
| 4.13.01.01 | Round hand railing system | m | 18
| 4.13.02 | c) FRP Grating
| 4.13.02.01 | 450 mm x 450 mm x 38 mm deep FRP grating | No. | 3
| 4.13.03 | e) FRP platforms including frames and supports
| 4.13.03.01 | 38 mm deep FRP grating platform | m² | 15
PSCC1.024 | 4.14 | Casting pipes and specials in concrete
| 4.14.01 | DN 600 Steel pipe cast into chamber wall | No. | 1
| 4.14.02 | DN 800 Steel pipe cast into chamber wall | No. | 2
PSCC1.025 | 4.15 | Installation of precast elements
| 4.15.01 | Precast roof slabs as per | No. | 4
Drawing: JW14358-16941-T-013-S30-00-TMS
| 4.15.02 | Precast roof slabs as per | No. | 4
Drawing: JW14358-16941-T-013-S32-00-TMS
| 4.15.03 | Precast roof slabs as per | No. | 5
Drawing: JW14358-16941-T-013-S51-00-TMS
Carried forward to summary (Part C - Section 5)
Part C - Section 5 - Hot-Tapping chambers: Node NA1, ND1, ND5
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SUMMARY
SANS 1200 C |  | SITE CLEARANCE
SANS 1200 DB |  | EARTHWORKS (PIPE TRENCHES)
SANS 1200 L |  | MEDIUM-PRESSURE PIPELINES
SANS 2001 CC1 |  | CONCRETE WORKS (STRUCTURAL)
Total carried forward to summary

## Butterfly Valves
Part C - Section 6 - Upgrades to Existing Butterfly Valve Chambers
Site Clearance
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 C | 1 | SITE CLEARANCE
Refer to Drawings:
JW14358-16941-T-013-S45-00-TMS
JW13038-16941-T-014-S46-00-TMS
JW14358-16941-T-013-S47-00-TMS
PSC 8.2.1 | 1.01 | Clear and grub
| 1.01.01 | Areas | m² | 40
8.2.10 | 1.02 | Remove topsoil to nominal depth of 150 mm and stockpile | m³ | 6
PSC 8.2.12 | 1.03 | Removal of man-made surfaces and kerbing
| 1.03.01 | c) Interlocking concrete segmental paving blocks, | m² | 30
PSC 8.2.14 | 1.03 | Take down and re-erect existing fences and
guardrails
| 1.03.01 | a) Guardrails | m | 15
| 1.03.02 | b) Diamond mesh fencing | m | 15
PSC 8.2.17 | 1.04 | Demolishing existing valve chambers
| 1.04.01 | a) Unreinforced concrete | m³ | 2
| 1.04.02 | b) Reinforced concrete | m³ | 8
| 1.04.03 | c) 220 mm Brick wall | m² | 40
PSC 8.2.18 | 1.05 | Temporary removal and reinstatement of precast concrete | No. | 5
slabs
PSC 8.2.19 | 1.06 | Temporary removal and reinstatement of precast concrete | No. | 1
bunkers
PSC 8.2.20 | 1.07 | Temporary disconnection and reconnection of cathodic | No. | 1
protection cabling inside precast concrete bunkers
Carried forward to summary (Part C - Section 6)
Part C - Section 6 - Upgrades to Existing Butterfly Valve Chambers
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 DB | 2 | EARTHWORKS (PIPE TRENCHES)
Refer to Drawings: JW14358-16941-T-013-S45-00-TMS, JW13038-16941-T-014-S46-00-TMS, JW14358-16941-T-013-S47-00-TMS
JW14358-16941-T-013-S45-00-TMS
JW13038-16941-T-014-S46-00-TMS
JW14358-16941-T-013-S47-00-TMS
PSDB 8.3.2 | 2.01 | Excavation
| 2.01.01 | d) Excavate in all materials for stormwater inlet and outlet | m³ | 30
structures and for manholes, catchpits, valve chambers
and the like, irrespective of depth, and backfill around
structures
| 2.01.02 | e) Extra over 2.01.01 for excavating in
| 2.01.02.01 | 1) intermediate material | m³ | 5
| 2.01.02.02 | 2) hard material | m³ | 5
| 2.01.03 | f) Hand excavation where ordered by the Project Manager
| 2.01.03.01 | a) Soft material | m³ | 5
| 2.01.03.02 | b) Intermediate material | m³ | 5
| 2.01.03.03 | c) Hard material | m³ | 5
| 2.01.04 | g) Backfill stabilized with 5% cement where directed by | m³ | 5
the Project Manager
| 2.01.05 | h) Soilcrete backfill where directed by the Project Manager | m³ | 5
Carried forward to summary (Part C - Section 6)
Part C - Section 6 - Upgrades to Existing Butterfly Valve Chambers
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 L | 3 | MEDIUM-PRESSURE PIPELINES
Refer to Drawings: JW14358-16941-T-013-S45-00-TMS, JW13038-16941-T-014-S46-00-TMS, JW14358-16941-T-013-S47-00-TMS
JW14358-16941-T-013-S45-00-TMS
JW13038-16941-T-014-S46-00-TMS
JW14358-16941-T-013-S47-00-TMS
8.2.5 | 3.01 | Supply and Place Pipes, Valves, and Specials
(Short pipe runs)
| 3.01.01 | Butterfly Valve Chamber 1
| 3.01.01.01 | Item 1: DN 1200 PN25 Butterfly Valve to BS5155 (Short | No. | 1
Body) / EN593 (Series 13); Boving or similar approved;
with loose EPDM liner approved for drinking water;
supplied with gearbox; flanged both ends; drilled to
SANS1123 Table 2500/3
| 3.01.01.02 | Item 2: Spool piece DN 1200 x 300 mm long; SANS 719; | No. | 1
wall thickness t = 10 mm; both ends flanged; drilled to
SANS 1123 Table 2500/3
| 3.01.02 | Butterfly Valve Chamber 2
| 3.01.02.01 | Item 1: DN 1200 PN25 Butterfly Valve to BS5155 (Short with loose EPDM liner approved for drinking water; | No. | 1
Body) / EN593 (Series 13); Boving or similar approved;
supplied with gearbox; flanged both ends; drilled to
SANS 1123 Table 2500/3
| 3.01.02.02 | Item 2: DN 300 PN25 wedge gate valve for vertical | No. | 1
operation; non rising spindle; anti-clockwise closing to
SANS 664; manually operated; Vosa or similar approved;
both ends flanged; flanges drilled to
SANS 1123 Table 2500/3
| 3.01.02.03 | Item 3: Spool piece DN 1200 x 300 mm long; SANS 719; | No. | 1
wall thickness t = 10 mm; both ends flanged; drilled to
SANS 1123 Table 2500/3
| 3.01.02.04 | Item 4: DN1200 x DN300 Scour Tee; wall thickness | No. | 2
t = 10 mm (DN1200) / t = 6 mm (DN300); length of
DN1200 section = 760 mm; all ends flanged; drilled to
SANS 1123 Table 2500/3
PSL 8.2.31 | 3.03 | Insitu repair of epoxy coated and lined pipe specials
| 3.03.01 | a) Flanges
| 3.03.01.01 | DN 300 flange | No. | 4
| 3.03.01.02 | DN 1200 flange | No. | 1
| 3.03.02 | b) Pipes
| 3.03.02.01 | DN 300 steel pipe | m² | 8
| 3.03.02.02 | DN 1200 steel pipe | m² | 15
Carried forward
Part C - Section 6 - Upgrades to Existing Butterfly Valve Chambers
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSL 8.2.32 | 3.04 | Replacement of Existing Valves and Specials under
Shutdown Conditions
| 3.04.01 | a) Butterfly Valve Chamber 1; Drawings: | Sum | 1
JW14358-16941-T-013-S45-00-TMS
JW14358-16941-T-013-S46-00-TMS
| 3.04.02 | b) Butterfly Valve Chamber 1; Drawing: | Sum | 1
JW14358-16941-T-013-S47-00-TMS
PSL 8.2.34 | 3.05 | Operation and Maintenance Manuals for Valves and
Flow Meters
| 3.05.01 | DN 1200 Butterfly Valve (PN25) | Sum | 1
Carried forward to summary (Part C - Section 6)
Part C - Section 6 - Upgrades to Existing Butterfly Valve Chambers
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 2001 | 4 | CONCRETE WORKS (STRUCTURAL)
PART CC1
Refer to Drawings: JW14358-16941-T-013-S45-00-TMS, JW13038-16941-T-014-S46-00-TMS, JW14358-16941-T-013-S47-00-TMS
JW14358-16941-T-013-S45-00-TMS
JW13038-16941-T-014-S46-00-TMS
JW14358-16941-T-013-S47-00-TMS
SCHEDULED FORMWORK ITEMS
PSCC1.002 | 4.01 | Smooth
| 4.01.01 | Vertical formwork to
| 4.01.01.01 | Walls | m² | 40
| 4.01.02 | Horizontal formwork to
| 4.01.02.01 | Slabs | m² | 40
PSCC1.005 | 4.02 | Narrow widths (up to 300 mm wide)
| 4.02.01 | Vertical Smooth formwork to
| 4.02.01.01 | Slabs | m | 50
PSCC1.006 | 4.03 | Box out holes/form voids:
| 4.03.01 | a) Small, circular, of diameter up to 0,35 m
| 4.03.01.01 | 0 m up to and including 0,5 m | No. | 20
| 4.03.02 | d) Large, other than circular, areas over 0.1 m2 up
to 2,0 m2
| 4.03.02.01 | 0 m up to and including 0,5 m | No. | 3
SCHEDULED REINFORCEMENT ITEMS
PSCC1.007 | 4.04 | Steel bars
| 4.04.01 | a) Steel bars irrespective of grade and diameter | t | 4
SCHEDULED CONCRETE ITEMS
PSCC1.012 | 4.05 | Strength concrete
| 4.05.01 | Class 30 MPa/19 mm concrete in
| 4.05.01.01 | Walls | m3 | 10
| 4.05.01.02 | Roof slabs | m3 | 10
Carried forward
Part C - Section 6 - Upgrades to Existing Butterfly Valve Chambers
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.013 | 4.06 | Unformed surface finishes
| 4.06.01 | a) Steel-floated finish
| 4.06.01.01 | Top of Walls | m² | 10
| 4.06.01.02 | Roof slabs | m² | 40
| 4.06.02 | e) Screed in 3:1 Sand and Cement Mix
| 4.06.02.01 | Chamber floor screed | m³ | 3
PSCC1.015 | 4.07 | Joints
| 4.07.01 | Polysulphide sealant between precast slabs | m | 60
PSCC1.018 | 4.08 | Grouting
| 4.08.01 | a) Under bases of pipe supports and straps | m³ | 2
PSCC1.019 | 4.09 | HD bolts and miscellaneous metal work as per drawing JW14358-16941-T-013-S45-00-TMS
Drawing: JW14358-16941-T-013-S45-00-TMS
| 4.09.01 | Fabricate and install galvanised mild steel ladders as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.09.02 | Fabricate and cast in long inlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.09.03 | Fabricate and cast in short outlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.09.04 | Fabricate and cast in galvanised access manholes as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.09.05 | Fabricate and cast in lifting hooks as per bolt detail on | No. | 8
Drawing: JW14358-16941-T-017-S10-00-TMS
Carried forward
Part C - Section 6 - Upgrades to Existing Butterfly Valve Chambers
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.019 | 4.10 | HD bolts and miscellaneous metal work as per drawing JW14358-16941-T-013-S45-00-TMS
Drawing: JW14358-16941-T-013-S45-00-TMS
| 4.10.01 | Fabricate and install galvanised mild steel ladders as per | No. | 2
Drawing:JW14358-16941-T-017-S09-00-TMS
| 4.10.02 | Fabricate and cast in long inlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.10.03 | Fabricate and cast in short outlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.10.04 | Fabricate and cast in galvanised access manholes as per | No. | 2
Drawing: JW14358-16941-T-017-S09-00-TMS
| 4.10.05 | Fabricate and cast in lifting hooks as per bolt detail on | No. | 8
Drawing: JW14358-16941-T-017-S10-00-TMS
PSCC1.020 | 4.11 | Colour Mitigation to
| 4.11.01 | Exposed Chambers along roadways | m² | 40
MISCELLANEOUS ITEMS
PSCC1.021 | 4.12 | Polythene sheeting under concrete
| 4.12.01 | 250 micron green medium density polyethylene | m² | 40
dampproof sheeting
PSCC1.023 | 4.13 | FRP items
| 4.13.01 | a) FRP Grating
| 4.13.01.01 | 450 mm x 450 mm x 38 mm deep FRP grating | m² | 3
PSCC1.025 | 4.14 | Installation of precast elements
| 4.14.01 | Precast roof slabs | No. | 3
PSCC1.027 | 4.15 | Masonry
| 4.15.01 | 110 mm brick wall | m² | 10
| 4.15.02 | 220 mm brick wall | m² | 20
Carried forward to summary (Part C - Section 6)
Part C - Section 6 - Upgrades to Existing Butterfly Valve Chambers
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SUMMARY
SANS 1200 C |  | SITE CLEARANCE
SANS 1200 DB |  | EARTHWORKS (PIPE TRENCHES)
SANS 1200 L |  | MEDIUM-PRESSURE PIPELINES
SANS 2001 CC1 |  | CONCRETE WORKS (STRUCTURAL)
Total carried forward to summary

## PRV and NRV
Part C - Section 7 - PRV, NRV and FM chamber: Node NA4, NB11, NC26, NC25
Site Clearance
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 C | 1 | SITE CLEARANCE
Refer to Drawings:
JW14358-16941-T-013-S17-00-TMS
JW14358-16941-T-013-S20-00-TMS
JW14358-16941-T-013-S42-00-TMS
JW14358-16941-T-013-S49-00-TMS
PSC 8.2.1 | 1.01 | Clear and grub
| 1.01.01 | Areas | m² | 500
8.2.2 | 1.02 | Remove and grub large trees and tree stumps of
girth
| 1.02.01 | Over 1 m and up to and including 2 m | No. | 10
8.2.10 | 1.03 | Remove topsoil to nominal depth of 150 mm and stockpile | m³ | 75
PSC 8.2.12 | 1.04 | Removal of man-made surfaces and kerbing
| 1.04.01 | a) Road materials with Asphalt ≤ 50mm thick | m² | 36
| 1.04.02 | c) Interlocking concrete segmental paving blocks | m² | 24
| 1.04.03 | h) Garden, lawns and grassing | m² | 550
PSC 8.2.14 | 1.05 | Take down and re-erect existing fences
and guardrails
| 1.05.01 | a) Guardrails | m | 20
| 1.05.02 | b) Diamond mesh fencing | m | 20
PSC 8.2.17 | 1.06 | Demolishing existing valve chambers
| 1.06.01 | b) Reinforced concrete | m³ | 15
| 1.06.02 | c) 220 mm Brick wall | m² | 36
Carried forward to summary (Part C - Section 7)
Part C - Section 7 - PRV, NRV and FM chamber: Node NA4, NB11, NC26, NC25
Eathworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 DB | 2 | EARTHWORKS (PIPE TRENCHES)
Refer to Drawings: JW14358-16941-T-013-S17-00-TMS, JW14358-16941-T-013-S20-00-TMS, JW14358-16941-T-013-S42-00-TMS, JW14358-16941-T-013-S49-00-TMS
JW14358-16941-T-013-S17-00-TMS
JW14358-16941-T-013-S20-00-TMS
JW14358-16941-T-013-S42-00-TMS
JW14358-16941-T-013-S49-00-TMS
PSDB 8.3.2 | 2.01 | Excavation
| 2.01.01 | d) Excavate in all materials for stormwater inlet and outlet structures | m³ | 1000
structures and for manholes, catchpits, valve chambers
and the like, irrespective of depth, and backfill around
structures
| 2.01.02 | e) Extra over 2.01.01 for excavating in
| 2.01.02.01 | 1) intermediate material | m³ | 100
| 2.01.02.02 | 2) hard material | m³ | 100
| 2.01.03 | f) Hand excavation where ordered by the Project Manager
| 2.01.03.01 | a) Soft material | m³ | 100
| 2.01.03.02 | b) Intermediate material | m³ | 100
| 2.01.03.03 | c) Hard material | m³ | 100
| 2.01.04 | g) Backfill stabilized with 5% cement where directed by | m³ | 200
the Project Manager
| 2.01.05 | h) Soilcrete backfill where directed by the Project | m³ | 200
Manager
Carried forward to summary (Part C - Section 7)
Part C - Section 7 - PRV, NRV and FM chamber: Node NA4, NB11, NC26, NC25
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 L | 4 | MEDIUM-PRESSURE PIPELINES
Refer to Drawings: JW14358-16941-T-013-S18-00-TMS, JW14358-16941-T-013-S21-00-TMS, JW14358-16941-T-013-S43-00-TMS, JW14358-16941-T-013-S50-00-TMS
JW14358-16941-T-013-S18-00-TMS
JW14358-16941-T-013-S21-00-TMS
JW14358-16941-T-013-S43-00-TMS
JW14358-16941-T-013-S50-00-TMS
PSL 8.2.1 | 3.01 | Supply, Lay, and Bed Pipes Complete with Couplings
| 3.01.01 | High-Impact mPVC Class 16 complete with shouldered
end coupling system
| 3.01.01.01 | Class 16 DN 160 | m | 30
8.2.2 | 3.02 | Extra-over 3.0.1 for the Supplying, Laying, and
Bedding of Specials Complete with Couplings
| 3.02.01 | High-Impact mPVC Class 16 bends complete with
shouldered end coupling system
| 3.02.01.01 | DN 160 11.25° bend | No. | 1
| 3.02.01.02 | DN 160 22.5° bend | No. | 1
| 3.02.01.03 | DN 160 45° bend | No. | 1
| 3.02.01.04 | DN 160 90° bend | No. | 1
| 3.02.02 | High-Impact mPVC Class 16 shouldered end repair
couplings
| 3.02.02.01 | DN 160 | No. | 2
| 3.02.03 | Flange adaptors for High-Impact mPVC Class 16
complete with shouldered end coupling system
| 3.02.03.01 | DN 160 | No. | 2
8.2.3 | 3.03 | Extra-over PSL 8.2.16 for Supplying, Fixing, and
Bedding of Valves
| 3.03.01 | DN 600 Pressure Reducing Valve Chamber 1
(Drawing: JW14358-16941-T-013-S21-00-TMS)
| 3.03.01.01 | Item 8: DN 300 PN25 wedge gate valve for vertical | No. | 4
operation; non rising spindle; anti-clockwise closing to
SANS 664; manually operated; Vosa or similar approved;
both ends flanged; flanges drilled to
SANS 1123 Table 2500/3
| 3.03.01.02 | Item 10: DN 300 PN25 Pressure Reducing Valve, flanged | No. | 2
both ends; drilled to SANS 1123 Table 2500/3
| 3.03.01.03 | Item 16: DN 100 PN25 Resilient Seal Gate valve; | No. | 1
rising spindle; anti-clockwise closing to SANS 664
non; manually operated; both ends flanged; flanges
drilled to SANS 1123 Table 2500/3
Carried forward
Part C - Section 7 - PRV, NRV and FM chamber: Node NA4, NB11, NC26, NC25
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 3.03.01.04 | Item 17: DN 100 PN25 Double orifice with anti-shock | No. | 1
orifice mechanism air release valve, Vent-O-Mat RBX or
similar approved; flanges drilled to
SANS 1123 Table 2500/3
| 3.03.01.05 | Item 17: DN 100 PN25 Double orifice with anti-shock | No. | 1
orifice mechanism air release valve, Vent-O-Mat RBX or
similar approved; flanges drilled to
SANS 1123 Table 2500/3
| 3.03.02 | DN 600 Bypass Pressure Reducing Valve Chamber
(Drawing JW14358-16941-T-013-S43-00-TMS)
| 3.03.02.01 | Item 5: DN 100 PN16 Double orifice with anti-shock | No. | 1
orifice mechanism air release valve, Vent-O-Mat RBX or
similar approved; flanges drilled to
SANS 1123 Table 1600/3
| 3.03.02.02 | Item 7: DN 300 PN16 wedge gate valve for vertical | No. | 2
operation; non rising spindle; anti-clockwise closing to
SANS 664; manually operated; Vosa or similar approved;
both ends flanged; flanges drilled to
SANS 1123 Table 1600/3
| 3.03.02.03 | Item 12: DN 300 PN16 Pressure Reducing Valve, flanged | No. | 1
both ends; drilled to SANS 1123 Table 1600/3
| 3.03.02.04 | Item 15: DN 150 PN16 Pressure Reducing Valve, flanged b | No. | 1
both ends to SANS 1123 Table 1600/3
| 3.03.02.05 | Item 16: DN 150 PN16 Resilient Seal Gate Valve; non | No. | 1
rising spindle; anti-clockwise closing to SANS 664;
non manually operated; both ends flanged; flanges
drilled to SANS 1123 Table 1600/3
| 3.03.02.06 | Item 17: DN 150 PN16 Resilient Seal Gate Valve; non | No. | 2
rising spindle; anti-clockwise closing to SANS 664;
non manually operated; both ends flanged; flanges
drilled to SANS 1123 Table 1600/3
| 3.03.03 | Existing DN 150 PRV Chamber Upgrade
(Drawing JW14358-16941-T-013-S50-00-TMS)
| 3.03.03.01 | Item 3: DN 100 PN 16 Resilient Seal Gate Valve; | No. | 1
rising spindle; anti-clockwise closing to SANS 664;
manually operated; both ends flanged; flanges drilled to
SANS 1123 Table 1600/3
| 3.03.03.02 | Item 8: DN 150 PN 16 Resilient Seal Gate Valve; non | No. | 1
rising spindle; anti-clockwise closing to SANS 664;
manually operated; both ends flanged; flanges drilled to
SANS 1123 Table 1600/3
| 3.03.03.03 | Item 10: DN 150 PN16 Pressure Reducing Valve, flanged | No. | 1
both ends; drilled to SANS 1123 Table 1600/3
Carried forward
Part C - Section 7 - PRV, NRV and FM chamber: Node NA4, NB11, NC26, NC25
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 3.03.04 | DN 200 Non-return Valve Chamber
(Drawing JW14358-16941-T-013-S18-00-TMS)
| 3.03.04.01 | Item 5: DN 100 PN16 Double orifice with anti-shock | No. | 1
orifice mechanism air release valve, Vent-O-Mat RBX or
similar approved; flanges drilled to
SANS 1123 Table 1600/3
| 3.03.04.02 | Item 7: DN 150 PN 16 Resilient Seal Gate Valve; non | No. | 4
rising spindle; anti-clockwise closing to SANS 664;
manually operated; both ends flanged; flanges drilled to
SANS 1123 Table 1600/3
| 3.03.04.03 | Item 13: DN 150 Single Door Swing Check Valve to | No. | 1
SANS 1551; Vosa or similar approved; flanged both ends;
drilled to SANS 1123 Table 1600/3
PSL 8.2.19 | 3.04 | Extra over 8.2.16 for the Supplying, Laying, Welding
or Jointing and Bedding of Steel specials
| 3.04.01 | DN 600 Pressure Reducing Valve Chamber 1
(Drawing JW14358-16941-T-013-S21-00-TMS)
| 3.04.01.01 | Item 1: Concentric reducer DN 600 to DN 300; | No. | 2
SANS 719; Wall Thickness t = 6 mm; 610 mm long;
both ends flanged; drilled to SANS 1123 Table 2500/3
| 3.04.01.02 | Item 2: Spool piece DN 300; 1450 mm long; SANS 719; | No. | 1
Wall Thickness t = 6 mm; both ends flanged; drilled to
SANS 1123 Table 2500/3; with puddle flange
| 3.04.01.03 | Item 3a: DN 300 Y-Strainer; Flanged both ends; drilled | No. | 2
to SANS 1123 Table 2500/3
| 3.04.01.04 | Item 3b: DN 300 T-Strainer; Flanged both ends; drilled | No. | 2
to SANS 1123 Table 2500/3
| 3.04.01.05 | Item 4: Dismantling joint DN 300; Flanged and drilled to | No. | 2
SANS 1123 Table 2500/3
| 3.04.01.06 | Item 5: Equal tee; DN 300 x DN 300; SANS 719; | No. | 3
wall thickness = 6 mm; flanged all ends; drilled to
SANS 1123 Table 2500/3
| 3.04.01.07 | Item 7: Medium Radius 90 degree DN300 bend; | No. | 4
SANS 719; wall thickness t = 6 mm; Flanged both ends;
drilled to SANS 1123 Table 2500/3
| 3.04.01.08 | Item 9: Spool piece DN 300; 725 mm long; SANS 719; | No. | 4
Wall Thickness t = 6 mm; both ends flanged; drilled to
SANS 1123 Table 2500/3; with pipe support
| 3.04.01.09 | Item 11: Spool piece DN 300; 1475 mm long; SANS 719; | No. | 1
Wall Thickness t = 6 mm; both ends flanged; drilled to
SANS 1123 Table 2500/3; with pipe support
Carried forward
Part C - Section 7 - PRV, NRV and FM chamber: Node NA4, NB11, NC26, NC25
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 3.04.01.10 | Item 13: Spool piece DN 300; 1426 mm long; SANS 719; | No. | 1
Wall Thickness t = 6 mm; both ends flanged; drilled to
SANS 1123 Table 2500/3; with puddle flange
| 3.04.01.11 | Item 14: Spool piece DN 100 x 200 mm long; SANS 62 | No. | 1
heavy class; one end flanged to SANS 1123
Table 2500/3; other end welded to DN200 blank flange
SANS 1123 Table 2500/8 with hole drilled for DN100 pipe
| 3.04.01.12 | Item 15: Spool piece DN 100 x 200 mm long; SANS 62 | No. | 1
heavy Class; both ends flanged; drilled to
SANS 1123 Table 2500/3
| 3.04.01.13 | Item 19: Spool piece DN 300 x 900 mm long; SANS 719; | No. | 1
Wall Thickness t = 6 mm; both ends flanged; drilled to
SANS 1123 Table 2500/3; with pipe support
| 3.04.01.14 | Item 20: Spool piece DN 600 x 500 mm long; SANS 719; | No. | 2
Wall Thickness t = 6 mm; one end flanged; drilled to
SANS 1123 Table 2500/3
| 3.04.02 | DN 600 Bypass Pressure Reducing Valve Chamber
(Drawing JW14358-16941-T-013-S43-00-TMS)
| 3.04.02.01 | Item 1: Spool piece DN 600 x 500 mm long; SANS 719; | No. | 2
Wall Thickness t = 6 mm; one end flanged; drilled to
SANS 1123 Table 1600/3
| 3.04.02.02 | Item 2: Concentric Reducer DN 600 to DN 300 ; | No. | 2
SANS 719; Wall Thickness t = 6 mm; 600 mm long;
both ends flanged; drilled to SANS 1123 Table 1600/3
| 3.04.02.03 | Item 3: Spool piece DN 300 x 1155 mm long SANS 719; | No. | 2
Wall Thickness t = 6 mm; both ends flanged; drilled to
SANS 1123 Table 1600/3; with puddle flange
| 3.04.02.04 | Item 4: Spool piece DN 100 x 200 mm long; SANS 62 | No. | 1
heavy class; one end flanged; drilled to
SANS 1123 Table 1600/3; other end welded to DN 150
blank flange; drilled to SANS 1123 Table 1600/8 with
hole drilled for DN 100 pipe
| 3.04.02.05 | Item 6: Unequal tee; DN 300 x DN 150; SANS 719; | No. | 2
wall thickness = 6 mm; flanged all ends; drilled to
SANS 1123 Table 1600/3
| 3.04.02.06 | Item 8: Spool piece DN 300 x 596 mm long SANS 719; | No. | 1
Wall Thickness t = 6 mm; both ends flanged; drilled to
SANS 1123 Table 1600/3; with pipe support
| 3.04.02.07 | Item 9a: DN 300 Y-Strainer; Flanged both ends; drilled to | No. | 1
SANS 1123 Table 1600/3
| 3.04.02.08 | Item 9b: DN 300 T-Strainer; Flanged both ends; drilled to | No. | 1
SANS 1123 Table 1600/3
Carried forward
Part C - Section 7 - PRV, NRV and FM chamber: Node NA4, NB11, NC26, NC25
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 3.04.02.09 | Item 10: Spool piece DN 300; 1060 mm long; SANS 719; | No. | 1
Wall Thickness t = 6 mm; both ends flanged; drilled to
SANS 1123 Table 1600/3; with pipe support
| 3.04.02.10 | Item 11: Spool piece DN 300; 500 mm long; SANS 719; | No. | 1
Wall Thickness t = 6 mm; both ends flanged; drilled to
SANS 1123 Table 1600/3; with pipe support
| 3.04.02.11 | Item 13: Unequal tee; DN 300 x DN 150; SANS 719 | No. | 1
wall thickness = 6 mm (DN 300) / SANS 62
heavy class (DN 150); flanged all ends; drilled to
SANS 1123 Table 1600/3; with pipe support
| 3.04.02.12 | Item 14: Bend DN 150; SANS 62 Heavy Class; both ends | No. | 2
flanged; drilled to SANS 1123 Table 1600/3
| 3.04.02.13 | Item 18: Spool piece DN 150; 552 mm long; SANS 62 | No. | 1
heavy class; both ends flanged; drilled to
SANS 1123 Table 1600/3; with pipe support
| 3.04.02.14 | Item 19a: DN 150 Y-Strainer; Flanged both ends; drilled | No. | 1
to SANS 1123 Table 1600/3
| 3.04.02.15 | Item 19b: DN 150 T-Strainer; Flanged both ends; drilled | No. | 1
to SANS 1123 Table 1600/3
| 3.04.02.16 | Item 20: Spool piece DN 150; 552 mm long; SANS 62 | No. | 1
heavy class; both ends flanged; drilled to
SANS 1123 Table 1600/3
| 3.04.02.17 | Item 21: Spool piece DN 150; 610 mm long; SANS 62 | No. | 1
heavy class; both ends flanged; drilled to
SANS 1123 Table 1600/3; with pipe support
| 3.04.02.18 | Item 22: Spool piece DN 150; 538 mm long; SANS 62 | No. | 1
eavy class; both ends flanged; drilled to
SANS 1123 Table 1600/3
| 3.04.02.19 | Item 23: Dismantling joint DN 150; Flanged; drilled to | No. | 1
SANS 1123 Table 1600/3
| 3.04.02.20 | Item 24: Dismantling joint DN 300; Flanged; drilled to | No. | 1
SANS 1123 Table 1600/3
| 3.04.03 | Existing DN 150 PRV Chamber Upgrade
(Drawing JW14358-16941-T-013-S50-00-TMS)
| 3.04.03.01 | Item 1: Spool piece DN 200; 1220 mm long; SANS 719; | No. | 2
Wall Thickness t = 6 mm; both ends flanged; drilled to
SANS 1123 Table 1600/3; with puddle flange
| 3.04.03.02 | Item 2: Unequal tee; DN 200 x DN 100; SANS 719 wall | No. | 1
thickness = 6 mm (DN 200) / SANS 62 medium class
(DN 100); flanged all ends; drilled to
SANS 1123 Table 1600/3
Carried forward
Part C - Section 7 - PRV, NRV and FM chamber: Node NA4, NB11, NC26, NC25
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 3.04.03.03 | Item 4: Spool piece DN 100; 1450 mm long; SANS 62 | No. | 1
medium class; both ends flanged; drilled to
SANS 1123 Table 1600/3
| 3.04.03.04 | Item 5: Equal tee; DN 200 x DN 200; SANS 719; wall | No. | 2
thickness t = 6 mm; flanged all ends; drilled to
SANS 1123 Table 1600/3
| 3.04.03.05 | Item 6: Spool piece DN 200; 1540 mm long; SANS 719; | No. | 3
Wall Thickness t = 6 mm; both ends flanged; drilled to
SANS 1123 Table 1600/3; with puddle flange
| 3.04.03.06 | Item 7: Concentric reducer DN 200 to DN 150; | No. | 4
SANS 719; Wall Thickness t = 6 mm; 300 mm long;
both ends flanged; drilled to SANS 1123 Table 1600/3
| 3.04.03.07 | Item 9: Spool piece DN 150; 320 mm long; SANS 62 | No. | 2
medium class; both ends flanged; drilled to
SANS 1123 Table 1600/3
| 3.04.03.08 | Item 11: Spool piece DN 150; 170 mm long; SANS 62 | No. | 1
medium class; both ends flanged; drilled to
SANS 1123 Table 1600/3
| 3.04.03.09 | Item 12: Dismantling joint DN 150; Flanged; drilled to | No. | 1
SANS 1123 Table 1600/3
| 3.04.03.10 | Item 13: Spool piece DN 150; 200 mm long; SANS 62 | No. | 1
medium class; both ends flanged; drilled to
SANS 1123 Table 1600/3; with pressure socket
| 3.04.03.11 | Item 14: Spool piece DN 150; 1420 mm long; SANS 62 | No. | 1
medium class; both ends flanged; drilled to
SANS 1123 Table 1600/3
| 3.04.03.12 | Item 15: DN 200 Flange adaptor for High-Impact mPVC | No. | 2
Class 16 complete with shouldered end coupling system
flange drilled to SANS 1123 Table 1600/3
| 3.04.03.13 | Item 16: DN 150 Flange adaptor for High-Impact mPVC | No. | 1
Class 16 complete with shouldered end coupling system
flange drilled to SANS 1123 Table 1600/3
| 3.04.03.14 | Item 17: DN 100 Flange adaptor for High-Impact mPVC | No. | 1
Class 16 complete with shouldered end coupling system
flange drilled to SANS 1123 Table 1600/3
| 3.04.04 | DN 200 Non-return Valve Chamber
(Drawing JW14358-16941-T-013-S18-00-TMS)
| 3.04.04.01 | Item 1: DN 200 Flange adaptor for High-Impact mPVC | No. | 2
Class 16 complete with shouldered end coupling system
flange drilled to SANS 1123 Table 1600/3
| 3.04.04.02 | Item 2: Spool piece DN 150; 1250 mm long; SANS 62 | No. | 1
medium class; both ends flanged; drilled to
SANS 1123 Table 1600/3
Carried forward
Part C - Section 7 - PRV, NRV and FM chamber: Node NA4, NB11, NC26, NC25
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 3.04.04.03 | Item 3: Concentric reducer DN 200 to DN 150; | No. | 2
SANS 719; Wall Thickness t = 6 mm; 180 mm long; both
ends flanged; drilled to SANS 1123 Table 1600/3
| 3.04.04.04 | Item 4: Spool piece DN 100 x 200 mm long; SANS 62 | No. | 1
heavy class; one end flanged; drilled to
SANS 1123 Table 1600/3; other end welded to DN 200
blank flange; drilled to SANS 1123 Table 1600/8 with
hole drilled for DN 100 pipe
| 3.04.04.05 | Item 6: Spool piece DN 150; 454 mm long; SANS 62 | No. | 1
medium class; both ends flanged; drilled to
SANS 1123 Table 1600/3
| 3.04.04.06 | Item 8: Spool piece DN 150; 773 mm long; SANS 62 | No. | 1
medium class; both ends flanged; drilled to
SANS 1123 Table 1600/3; with pipe support
| 3.04.04.07 | Item 9a: DN 150 Y-Strainer; Flanged both ends; drilled to | No. | 1
SANS 1123 Table 1600/3
| 3.04.04.08 | Item 9b: DN 150 T-Strainer; Flanged both ends; drilled to | No. | 1
SANS 1123 Table 1600/3
| 3.04.04.09 | Item 12: Spool piece DN 150; 830 mm long; SANS 62 | No. | 2
medium class; both ends flanged; drilled to
SANS 1123 Table 1600/3; with pipe support
| 3.04.04.10 | Item 15: Spool piece DN 150; 1038 mm long; SANS 62 | No. | 1
medium class; both ends flanged; drilled to
SANS 1123 Table 1600/3; with puddle flange
| 3.04.04.11 | Item 17: Spool piece DN 150; 1256 mm long; SANS 62 | No. | 1
medium class; both ends flanged; drilled to
SANS 1123 Table 1600/3; with puddle flange
| 3.04.04.12 | Item 18a: DN 160 PE100 PN16 HDPE stub flange with | No. | 1
backing ring
| 3.04.04.13 | Item 18b: DN 150 Flange adaptor for High-Impact mPVC | No. | 1
Class 16 complete with shouldered end coupling system;
Flange drilled to SANS 1123 Table 1600/3
| 3.04.04.14 | Item 19: Equal tee; DN 150 x DN 150; SANS 62 medium | No. | 1
class; flanged all ends; drilled to
SANS 1123 Table 1600/3; with pipe support
| 3.04.04.15 | Item 20: Equal tee; DN 150 x DN 150; SANS 62 medium | No. | 1
class; flanged all ends; drilled to
SANS 1123 Table 1600/3
Carried forward
Part C - Section 7 - PRV, NRV and FM chamber: Node NA4, NB11, NC26, NC25
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSL 8.2.30 | 3.05 | Extra over 8.2.16 for for the Supplying, Installing and
Commissioning of Flow Meters
| 3.05.01 | DN 600 Pressure Reducing Valve Chamber 1
(Drawing JW14358-16941-T-013-S21-00-TMS)
| 3.05.01.01 | Item 12: DN 300 PN25 Electromagnetic flow meter | No. | 1
complete with sensor and remotely mounted transmitter;
flanges drilled to SANS 1123 Table 2500/3; supplied with
15 m of cable
PSL 8.2.33 | 3.06 | Supplying, Installing and Commissioning Pressure | No. | 10
transmitters with GSM Battery operated data loggers
PSL 8.2.34 | 3.07 | Operation and Maintenance Manuals for Valves and
Flow Meters
| 3.07.01 | DN 100 Resilient Seal Gate Valve (PN25) | Sum | 1
| 3.07.02 | DN 150 Resilient Seal Gate Valve (PN16) | Sum | 1
| 3.07.03 | DN 300 Wedge Gate Valve (PN16) | Sum | 1
| 3.07.04 | DN 300 Wedge Gate Valve (PN25) | Sum | 1
| 3.07.05 | DN 100 Air Valve (PN25) | Sum | 1
| 3.07.06 | DN 150 Pressure Reducing Valve (PN16) | Sum | 1
| 3.07.07 | DN 300 Pressure Reducing Valve (PN16) | Sum | 1
| 3.07.08 | DN 300 Pressure Reducing Valve (PN25) | Sum | 1
| 3.07.09 | DN 150 Y-type Strainer (PN16) | Sum | 1
| 3.07.10 | DN 150 T-type Strainer (PN16) | Sum | 1
| 3.07.11 | DN 300 Y-type Strainer (PN16) | Sum | 1
| 3.07.12 | DN 300 T-type Strainer (PN16) | Sum | 1
| 3.07.13 | DN 300 Y-type Strainer (PN25) | Sum | 1
| 3.07.14 | DN 300 T-type Strainer (PN25) | Sum | 1
| 3.07.15 | DN 150 Resilient Seal Gate Valve (PN16) | Sum | 1
Carried forward to summary (Part C - Section 7)
Part C - Section 7 - PRV, NRV and FM chamber: Node NA4, NB11, NC26, NC25
Cable Ducts
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 LC | 4 | CABLE DUCTS
Refer to Drawing: JW14358-16941-T-013-S20-00-TMS
JW14358-16941-T-013-S17-00-TMS
JW14358-16941-T-013-S20-00-TMS
JW14358-16941-T-013-S42-00-TMS
JW14358-16941-T-013-S49-00-TMS
8.2.2 | 4.01 | Excavation
| 4.01.01 | a) Excavate in all materials for trenches, backfill,
compact and dispose of surplus material
| 4.01.01.01 | i) Single duct trench (300 mm wide), up to 1 m deep | m3 | 5
PSLC 8.2.5 | 4.02 | Supply, lay, bed and prove duct, including
draw wire and screening wire
| 4.02.01 | a) 110mm flexible conduit | m | 10
8.2.6 | 4.03 | Imported bedding material, where ordered
| 4.03.01 | a) Selected granular material | m3 | 3
Carried forward to summary (Part C - Section 7)
Part C - Section 7 - PRV, NRV and FM chamber: Node NA4, NB11, NC26, NC25
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 2001 | 5 | CONCRETE WORKS (STRUCTURAL)
PART CC1
Refer to Drawings: JW14358-16941-T-013-S17-00-TMS, JW14358-16941-T-013-S20-00-TMS, JW14358-16941-T-013-S42-00-TMS, JW14358-16941-T-013-S49-00-TMS
JW14358-16941-T-013-S17-00-TMS
JW14358-16941-T-013-S20-00-TMS
JW14358-16941-T-013-S42-00-TMS
JW14358-16941-T-013-S49-00-TMS
SCHEDULED FORMWORK ITEMS
PSCC1.002 | 5.01 | Smooth
| 5.01.01 | Vertical formwork to
| 5.01.01.01 | Foundations (Floor) | m² | 30
| 5.01.01.02 | Plinths | m² | 10
| 5.01.01.03 | Walls | m² | 620
| 5.01.01.04 | Sump | m² | 5
| 5.01.01.05 | Stairs | m² | 44
| 5.02.01 | Horizontal formwork to
| 5.02.01.01 | Precast roof slabs | m² | 120
PSCC1.005 | 5.02 | Narrow widths (up to 300 mm wide)
| 5.02.01 | Vertical Smooth formwork to
| 5.02.01.01 | Precast slabs | m | 265
| 5.02.01.02 | Concrete Bunker Apron Slab | m | 10
PSCC1.006 | 5.03 | Box out holes/form voids
| 5.03.01 | a) Small, circular, of diameter up to 0,35 m
| 5.03.01.01 | 0 m up to and including 0,5 m | No. | 60
| 5.03.02 | d) Large, other than circular, areas over 0.1 m2
up to 2,0 m2
| 5.03.02.01 | 0 m up to and including 0,5 m | No. | 6
| 5.03.02.02 | Over 2,0 m deep | No. | 12
SCHEDULED REINFORCEMENT ITEMS
PSCC1.007 | 5.04 | Steel bars
| 5.04.01 | a) Steel bars irrespective of grade and diameter | t | 45
Carried forward
Part C - Section 7 - PRV, NRV and FM chamber: Node NA4, NB11, NC26, NC25
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
SCHEDULED CONCRETE ITEMS
PSCC1.011 | 5.05 | Blinding layer in Grade 15 MPa/19 mm concrete
| 5.05.01 | 50 mm thickness | m² | 265
PSCC1.012 | 5.06 | Strength concrete
| 5.06.01 | Class 30 MPa/19 mm concrete in
| 5.06.01.01 | Foundations (Floor) | m3 | 40
| 5.06.01.02 | Plinths | m3 | 8
| 5.06.01.03 | Walls | m3 | 100
| 5.06.01.04 | Roof slabs | m3 | 36
| 5.06.01.05 | Sump | m3 | 4
| 5.06.01.06 | Stairs | m3 | 17
| 5.06.01.07 | Concrete Bunker Apron Slab | m3 | 1
PSCC1.013 | 5.07 | Unformed surface finishes
| 5.07.01 | a) Steel-floated finish
| 5.07.01.01 | Foundations (Floor) | m² | 150
| 5.07.01.02 | Top of Plinths | m² | 11
| 5.07.01.03 | Top of Walls | m² | 25
| 5.07.01.04 | Roof slabs | m² | 120
| 5.07.01.05 | Concrete Bunker Apron Slab | m² | 10
| 5.07.02 | d) Broomed finish
| 5.07.02.01 | Blinding layer | m² | 265
| 5.07.03 | e) Screed in 3:1 Sand and Cement Mix
| 5.07.03.01 | Chamber floor screed | m³ | 15
PSCC1.015 | 5.08 | Manufacture (or supply) and erect precast units
| 5.08.01 | Concrete Bunker (Minimum Internal Dimensions: | No. | 1
680 H x 500 W x 375 D)
PSCC1.017 | 5.09 | Joints
| 5.09.01 | Polysulphide sealant between precast slabs | m | 105
Carried forward
Part C - Section 7 - PRV, NRV and FM chamber: Node NA4, NB11, NC26, NC25
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.018 | 5.10 | Grouting
| 5.10.01 | a) Under bases of pipe supports and straps | m³ | 5
| 5.10.02 | c) Pipe box-outs | m³ | 5
PSCC1.019 | 5.11 | HD bolts and miscellaneous metal work
| 5.11.01 | Metal work for DN 600 Pressure Reducing Valve
Chamber 1
(Drawing JW14358-16941-T-013-S21-00-TMS)
| 5.11.01.01 | Fabricate and install galvanised mild steel ladders as per | No. | 2
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.01.02 | Fabricate and cast in long inlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.01.03 | Fabricate and cast in short outlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.01.04 | Fabricate and cast in galvanised access manholes as per | No. | 2
Drawing:JW14358-16941-T-017-S09-00-TMS
| 5.11.01.05 | Fabricate and cast in lifting hooks as per bolt detail on | No. | 32
Drawing: JW14358-16941-T-017-S10-00-TMS
| 5.11.02 | Metal work for DN 600 Bypass Pressure Reducing Valve
Chamber
(Drawing JW14358-16941-T-013-S43-00-TMS)
| 5.11.02.01 | Fabricate and install galvanised mild steel ladders as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.02.02 | Fabricate and cast in long inlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.02.03 | Fabricate and cast in short outlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.02.04 | Fabricate and cast in galvanised access manholes as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.02.05 | Fabricate and cast in lifting hooks as per bolt detail on | No. | 20
Drawing: JW14358-16941-T-017-S10-00-TMS
| 5.11.02.06 | Fabricate and install DN 160 galvanised medium duty pipe | No. | 3
clamps as per
Drawing: JW14358-16941-T-017-S10-00-TMS
| 5.11.03 | Metal work for Existing DN 150 PRV Chamber Upgrade
(Drawing JW14358-16941-T-013-S50-00-TMS)
| 5.11.03.01 | Fabricate and install galvanised mild steel ladders as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
Carried forward
Part C - Section 7 - PRV, NRV and FM chamber: Node NA4, NB11, NC26, NC25
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 5.11.03.02 | Fabricate and install DN 160 galvanised medium duty pipe | No. | 3
clamps as per
Drawing: JW14358-16941-T-017-S10-00-TMS
| 5.11.03.03 | Fabricate and install DN 200 galvanised medium duty pipe | No. | 3
clamps as per
Drawing: JW14358-16941-T-017-S10-00-TMS
| 5.11.04 | Metal work for DN 200 Non-return Valve Chamber
(Drawing JW14358-16941-T-013-S18-00-TMS)
| 5.11.04.01 | Fabricate and install galvanised mild steel ladders as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.04.02 | Fabricate and cast in long inlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.04.03 | Fabricate and cast in short outlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.04.04 | Fabricate and cast in galvanised access manholes as per | No. | 1
Drawing:JW14358-16941-T-017-S09-00-TMS
| 5.11.04.05 | Fabricate and cast in lifting hooks as per bolt detail on | No. | 20
Drawing:JW14358-16941-T-017-S10-00-TMS
| 5.11.04.06 | Fabricate and install DN 160 galvanised medium duty pipe | No. | 3
clamps as per
Drawing:JW14358-16941-T-017-S10-00-TMS
PSCC1.020 | 5.12 | Colour Mitigation to
| 5.12.01 | Exposed Chambers along roadways | m² | 300
MISCELLANEOUS ITEMS
PSCC1.021 | 5.13 | Polythene sheeting under concrete
| 5.13.01 | 250 micron green medium density polyethylene | m² | 265
dampproof sheeting
PSCC1.023 | 5.14 | FRP items
| 5.14.01 | a) FRP Grating
| 5.14.01.01 | 450 mm x 450 mm x 38 mm deep FRP grating | No. | 5
PSCC1.024 | 5.15 | Casting pipes and specials in concrete
| 5.15.01 | DN 100 Steel pipe cast into chamber wall | No. | 2
| 5.15.02 | DN 150 Steel pipe cast into chamber wall | No. | 6
| 5.15.03 | DN 200 Steel pipe cast into chamber wall | No. | 6
| 5.15.04 | DN 300 Steel pipe cast into chamber wall | No. | 6
Carried forward
Part C - Section 7 - PRV, NRV and FM chamber: Node NA4, NB11, NC26, NC25
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.025 | 5.16 | Installation of precast elements
| 5.16.01 | Precast roof slabs as per | No. | 6
Drawing: JW14358-16941-T-013-S17-00-TMS
| 5.16.02 | Precast roof slabs as per | No. | 9
Drawing: JW14358-16941-T-013-S20-00-TMS
| 5.16.03 | Precast roof slabs as per drawing | No. | 6
Drawing: JW14358-16941-T-013-S42-00-TMS
PSCC1.026 | 5.17 | Drilling cores through concrete
| 5.17.02 | 100 mm diameter core through 250 mm thick concrete slab | No. | 10
PSCC1.027 | 5.18 | Masonry
| 5.18.01 | 110 mm brick wall | m² | 10
| 5.18.02 | 220 mm brick wall | m² | 30
Carried forward to summary (Part C - Section 7)
Part C - Section 7 - PRV, NRV and FM chamber: Node NA4, NB11, NC26, NC25
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SUMMARY
SANS 1200 C |  | SITE CLEARANCE
SANS 1200 DB |  | EARTHWORKS (PIPE TRENCHES)
SANS 1200 L |  | MEDIUM-PRESSURE PIPELINES
SANS 1200 LC |  | CABLE DUCTS
SANS 2001 CC1 |  | CONCRETE WORKS (STRUCTURAL)
Total carried forward to summary

## Tie-in Chambers
Part C - Section 8 - Tie-in chambers: Node NA103, NB12
Site Clearance
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 C | 1 | SITE CLEARANCE
Refer to Drawings:
JW14358-16941-T-013-S26-00-TMS
JW14358-16941-T-013-S35-00-TMS
PSC 8.2.1 | 1.01 | Clear and grub
| 1.01.01 | Areas | m² | 270
8.2.2 | 1.02 | Remove and grub large trees and tree stumps of
girth
| 1.02.01 | Over 1 m and up to and including 2 m | No. | 2
8.2.10 | 1.03 | Remove topsoil to nominal depth of 150 mm and stockpile | m³ | 40
PSC 8.2.14 | 1.04 | Take down and re-erect existing fences and guardrails
| 1.04.01 | a) Guardrails | m | 15
| 1.04.02 | b) Diamond mesh fencing | m | 15
Carried forward to summary (Part C - Section 8)
Part C - Section 8 - Tie-in chambers: Node NA103, NB12
Earthworks (pipe trenches)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 DB | 2 | EARTHWORKS (PIPE TRENCHES)
Refer to Drawings: JW14358-16941-T-013-S26-00-TMS, JW14358-16941-T-013-S35-00-TMS
JW14358-16941-T-013-S26-00-TMS
JW14358-16941-T-013-S35-00-TMS
PSDB 8.3.2 | 2.01 | Excavation
| 2.01.01 | d) Excavate in all materials for stormwater inlet and outlet | m³ | 600
structures and for manholes, catchpits, valve chambers
and the like, irrespective of depth, and backfill around
structures
| 2.01.02 | e) Extra over 2.01.01 for excavating in
| 2.01.02.01 | 1) intermediate material | m³ | 60
| 2.01.02.02 | 2) hard material | m³ | 60
| 2.01.03 | f) Hand excavation where ordered by the Project
Manager
| 2.01.03.01 | a) Soft material | m³ | 60
| 2.01.03.02 | b) Intermediate material | m³ | 60
| 2.01.03.03 | c) Hard material | m³ | 60
| 2.01.04 | g) Backfill stabilized with 5% cement where directed by | m³ | 120
the Project Manager
| 2.01.05 | h) Soilcrete backfill where directed by the Project | m³ | 120
Manager
Carried forward to summary (Part C - Section 8)
Part C - Section 8 - Tie-in chambers: Node NA103, NB12
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 L | 3 | MEDIUM-PRESSURE PIPELINES
Refer to Drawings: JW14358-16941-T-013-S27-00-TMS, JW14358-16941-T-013-S36-00-TMS
JW14358-16941-T-013-S27-00-TMS
JW14358-16941-T-013-S36-00-TMS
PSL 8.2.1 | 3.01 | Supply, Lay, and Bed Pipes Complete with Couplings
| 3.01.01 | High-Impact mPVC Class 16 complete with shouldered
end coupling system
| 3.01.01.01 | Class 16 DN 200 | m | 100
8.2.2 | 3.02 | Extra-over 3.0.1 for the Supplying, Laying, and
Bedding of Specials Complete with Couplings
| 3.02.01 | High-Impact mPVC Class 16 bends complete with
shouldered end coupling system
| 3.02.01.01 | DN 200, 11.25° bend | No. | 2
| 3.02.01.02 | DN 200, 22.5° bend | No. | 2
| 3.02.01.03 | DN 200, 45° bend | No. | 2
| 3.02.01.04 | DN 200, 90° bend | No. | 2
| 3.02.02 | High-Impact mPVC Class 16 shouldered end repair
couplings
| 3.02.02.01 | DN 200 | No. | 2
| 3.02.03 | Flange adaptors for High-Impact mPVC Class 16
complete with shouldered end coupling system
| 3.02.03.01 | DN 200 | No. | 2
8.2.3 | 3.03 | Extra-over PSL 8.2.16 for Supplying, Fixing, and
Bedding of Valves
| 3.03.01 | DN 600 Tie-in Chamber 2
(Drawing JW14358-16941-T-013-S27-00-TMS)
| 3.03.01.01 | Item 5: DN 100 PN16 Resilient Seal Gate valve; non rising | No. | 2
spindle; anti-clockwise closing to SANS 664; manually
operated; both ends flanged; flanges drilled to
SANS 1123 Table 1600/3
| 3.03.01.02 | Item 7: DN 100 PN16 Double orifice with anti-shock approved; | No. | 2
orifice mechanism air release valve, Vent-O-Mat RBX
or similar; flanges drilled to SANS 1123 Table 1600/3
| 3.03.01.03 | Item 9: DN 600 PN16 wedge gate valve for vertical | No. | 2
operation; non rising spindle; anti-clockwise closing to
SANS 664; manually operated; Vosa or similar approved;
both ends flanged; flanges drilled to
SANS 1123 Table 1600/3
Carried forward
Part C - Section 8 - Tie-in chambers: Node NA103, NB12
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 3.03.02 | DN 400 Tie-in Chamber
| 3.03.02.01 | Item 3: DN 400 PN16 wedge gate valve for vertical to | No. | 2
operation; non rising spindle; anti-clockwise closing to
SANS 664; manually operated; Vosa or similar
approved; both ends flanged; flanges drilled
SANS 1123 Table 1600/3
| 3.03.02.02 | Item 6: DN 400 PN16 Single Door Swing Check Valve to | No. | 1
SANS 1551; flanged both ends; drilled to
SANS 1123 Table 1600/3
| 3.03.02.03 | Item 16: DN 100 PN16 Resilient Seal Gate valve; non | No. | 1
rising spindle; anti-clockwise closing to SANS 664;
manually operated; both ends flanged; flanges drilled to
SANS 1123 Table 1600/3
| 3.03.02.04 | Item 17: DN 100 PN16 Double orifice with anti-shock | No. | 1
orifice mechanism air release valve, Vent-O-Mat RBX
or similar approved; flanges drilled to
SANS 1123 Table 1600/3
| 3.03.02.05 | Item 19: DN 200 PN16 wedge gate valve for vertical | No. | 1
operation; non rising spindle; anti-clockwise closing to
SANS 664; manually operated; Vosa or similar
approved; both ends flanged; flanges drilled to
SANS 1123 Table 1600/3
PSL 8.2.19 | 3.04 | Extra over 8.2.16 for the Supplying, Laying, Welding
or Jointing and Bedding of Steel specials
| 3.04.01 | Specials for DN 600 Tie-in Chamber 2 as per
Drawing: JW14358-16941-T-013-S27-00-TMS
| 3.04.01.01 | Item 1: Concentric reducer DN 600 to DN 400; SANS 719; | No. | 2
Wall Thickness t = 6 mm; 610 mm long; both ends
flanged to SANS 1123 Table 1600/3
| 3.04.01.02 | Item 2: Spool piece DN 400; 1260 mm long; SANS 719; | No. | 1
Wall Thickness t = 6 mm; both ends flanged to
SANS 1123 Table 1600/3; with puddle flange
| 3.04.01.03 | Item 4: Spool piece DN 100 x 200 mm long; SANS 62 | No. | 2
medium class; one end flanged to SANS 1123
Table 1600/3; other end welded to DN200 blank
flange to SANS 1123 Table 1600/8 with hole
drilled for DN100 pipe
| 3.04.01.04 | Item 6: Spool piece DN 100 x 200 mm long; SANS 62 | No. | 2
medium class; both ends flanged to
SANS 1123 Table 1600/3
| 3.04.01.05 | Item 8: Dismantling joint DN 400; flanged to | No. | 1
SANS 1123 Table 1600/3
Carried forward
Part C - Section 8 - Tie-in chambers: Node NA103, NB12
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 3.04.01.06 | Item 10: Spool piece DN 400 x 1200 mm long; SANS 719; | No. | 1
Wall Thickness t = 6 mm; both ends flanged to
SANS 1123 Table 1600/3; with pressure testing socket
| 3.04.01.07 | Item 12: Spool piece DN 400; 2000 mm long; SANS 719; | No. | 1
Wall Thickness t = 6 mm; both ends flanged to
SANS 1123 Table 1600/3; with pipe support
| 3.04.01.08 | Item 13a: DN 400 Y-Strainer; Flanged both ends to | No. | 1
SANS 1123 Table 1600/3
| 3.04.01.09 | Item 13b: DN 400 T-Strainer; Flanged both ends to | No. | 1
SANS 1123 Table 1600/3
| 3.04.01.10 | Item 14: Spool piece DN 400; 1278 mm long; SANS 719; | No. | 1
Wall Thickness t = 6 mm; both ends flanged to
SANS 1123 Table 1600/3; with puddle flange
| 3.04.01.11 | Item 15: DN 600 90 degree 4 segment medium radius | No. | 1
bend; SANS 719; Wall Thickness t = 6 mm; both ends
flanged to SANS 1123 Table 1600/3
| 3.04.01.12 | Item 16: Equal tee; DN 400 x DN 400 SANS 719; wall | No. | 1
thickness = 6 mm; flanged all ends to
SANS 1123 Table 1600/3; with pipe support
| 3.04.01.13 | Item 17: Spool piece DN 400; 1052 mm long; SANS 719; | No. | 1
Wall Thickness t = 6 mm; both ends flanged to
SANS 1123 Table 1600/3; with pipe support
| 3.04.01.14 | Item 18: Unequal tee; DN 400 x DN 300 SANS 719; wall | No. | 2
thickness = 6 mm; flanged all ends to
SANS 1123 Table 1600/3; with pipe support
| 3.04.01.15 | Item 19: Spool piece DN 400; 1317 mm long; SANS 719; | No. | 1
Wall Thickness t = 6 mm; both ends flanged to
SANS 1123 Table 1600/3; with puddle flange
| 3.04.01.16 | Item 20: DN 400 90 degree 4 segment medium radius | No. | 1
bend; SANS 719; Wall Thickness t = 6 mm; both ends
flanged to SANS 1123 Table 1600/3
| 3.04.01.17 | Item 21: Concentric reducer DN 500 to DN 400; | No. | 1
SANS 719; Wall Thickness t = 6 mm; 510 mm long;
both ends flanged to SANS 1123 Table 1600/3
| 3.04.02 | Specials for DN 400 Tie-in Chamber as per
Drawing:JW14358-16941-T-013-S36-00-TMS
| 3.04.02.01 | Item 1: Unequal tee; DN 400 x DN 300; SANS 719; Wall | No. | 2
Thickness = 6 mm; flanged all ends to
SANS 1123 Table 1600/3
| 3.04.02.02 | Item 2: Spool piece DN 400; 1260 mm long; SANS 719; | No. | 1
Wall Thickness t = 6 mm; both ends flanged to
SANS 1123 Table 1600/3; with puddle flange
Carried forward
Part C - Section 8 - Tie-in chambers: Node NA103, NB12
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| 3.04.02.03 | Item 4: Unequal tee; DN 400 x DN 200; SANS 719; wall | No. | 1
thickness = 6 mm; flanged all ends to
SANS 1123 Table 1600/3
| 3.04.02.04 | Item 5: Spool piece DN 400; 1070 mm long; SANS 719; | No. | 1
wall thickness t = 6 mm; both ends flanged to
SANS 1123 Table 1600/3; with pipe support
| 3.04.02.05 | Item 7: Spool piece DN 400; 846 mm long; SANS 719; | No. | 1
wall thickness t = 6 mm; both ends flanged to
SANS 1123 Table 1600/3; with pipe support
| 3.04.02.06 | Item 8: Equal tee; DN 400 x DN 400; SANS 719; wall | No. | 1
thickness = 6 mm; flanged all ends to
SANS 1123 Table 1600/3
| 3.04.02.07 | Item 9: Spool piece DN 400; 1052 mm long; SANS 719; | No. | 1
wall thickness t = 6 mm; both ends flanged to
SANS 1123 Table 1600/3; with pipe support
| 3.04.02.08 | Item 10: Spool piece DN 400; 1317 mm long; SANS 719; | No. | 1
wall thickness t = 6 mm; both ends flanged to
SANS 1123 Table 1600/3; with puddle flange
| 3.04.02.09 | Item 11: Spool piece DN 400; 1889 mm long; SANS 719; | No. | 1
wall thickness t = 6 mm; both ends flanged to
SANS 1123 Table 1600/3; with puddle flange
| 3.04.02.10 | Item 12: Concentric reducer DN 600 to DN 400; | No. | 1
SANS 719; Wall Thickness t = 6 mm; 610 mm long;
both ends flanged to SANS 1123 Table 1600/3
| 3.04.02.11 | Item 13: Spool piece DN 600; 500 mm long; SANS 719; | No. | 1
wall thickness t = 6 mm; one end flanged to
SANS 1123 Table 1600/3
| 3.04.02.12 | Item 14: Unequal tee; DN 200 x DN 100; SANS 719; wall | No. | 1
thickness = 6 mm (DN 200) / SANS 62 medium class
(DN 100); flanged all ends to SANS 1123 Table 1600/3;
with pipe support
| 3.04.02.13 | Item 15: Spool piece; DN100 x 200 mm long; SANS 62 | No. | 1
medium class; flanged both ends to
SANS 1123 Table 1600/3
| 3.04.02.14 | Item 18: Spool piece DN 200; 1284 mm long; SANS 719; | No. | 1
wall thickness t = 6 mm; both ends flanged to
SANS 1123 Table 1600/3
| 3.04.02.15 | Item 20: DN 300 Blank flange to | No. | 2
SANS 1123 Table 1600/8
| 3.04.02.15 | Item 21: DN 400 Loose flange drilled to | No. | 2
SANS 1123 Table 1600/3
Carried forward
Part C - Section 8 - Tie-in chambers: Node NA103, NB12
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSL 8.2.20 | 3.05 | Supply, Lay and Bed HDPE Pipes Complete with
Welded Joints
| 3.05.01 | PN16 PE100 HDPE pipe
| 3.05.01.01 | PN16 DN 315 mm | m | 40
PSL 8.2.21 | 3.06 | Extra over 4.05 for the Supplying, Laying, Butt Fusion
Welding and Bedding of HDPE specials
| 3.06.01 | PN16 PE100 HDPE bends
| 3.06.01.01 | DN 315mm, 11.25° bend | No. | 2
| 3.06.01.02 | DN 315 mm, 22.5° bend | No. | 2
| 3.06.01.03 | DN 315 mm, 45° bend | No. | 2
| 3.06.02 | PN16 HDPE stub flange and backing ring
| 3.06.02.01 | DN 315 mm | No. | 2
PSL 8.2.27 | 3.07 | Connect to Existing Mains
| 3.07.01 | a) Tie-in of new DN 400 chamber on existing DN 400 | sum | 1
(drawing JW14358-16941-T-013-S35-00-TMS)
PSL 8.2.30 | 3.08 | Extra over 8.2.16 for for the Supplying, Installing and
Commissioning of Flow Meters
| 3.08.01 | Item 11: DN 400 PN16 Electromagnetic flow meter | No. | 1
complete with sensor and remotely mounted transmitter;
flanges drilled to SANS 1123 Table 1600/3;
supplied with 15 m of cable
PSL 8.2.34 | 3.09 | Operation and Maintenance Manuals for Valves and
Flow Meters
| 3.09.01 | a) DN 200 Wedge Gate Valve (PN16) | Sum | 1
| 3.09.02 | b) DN 400 Wedge Gate Valve (PN16) | Sum | 1
| 3.09.03 | c) DN 400 Swing type Check Valve (PN16) | Sum | 1
| 3.09.04 | d) DN 400 Electromagnetic Flow Meter (PN16) | Sum | 1
Carried forward to summary (Part C - Section 8)
Part C - Section 8 - Tie-in chambers: Node NA103, NB12
Cable ducts
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 LC | 4 | CABLE DUCTS
Refer to Drawing: JW14358-16941-T-013-S26-00-TMS
JW14358-16941-T-013-S35-00-TMS
8.2.2 | 4.01 | Excavation
| 4.01.01 | a) Excavate in all materials for trenches, backfill,
compact and dispose of surplus material
| 4.01.01.01 | i) Single duct trench (300 mm wide), up to 1 m deep | m3 | 5
PSLC 8.2.5 | 4.02 | Supply, lay, bed and prove duct, including draw wire
and screening wire
| 4.02.01 | a) 110mm flexible conduit | m | 10
8.2.6 | 4.03 | Imported bedding material, where ordered
| 4.03.01 | a) Selected granular material | m3 | 3
Carried forward to summary (Part C - Section 8)
Part C - Section 8 - Tie-in chambers: Node NA103, NB12
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 2001 | 5.00 | CONCRETE WORKS (STRUCTURAL)
PART CC1
SCHEDULED FORMWORK ITEMS
PSCC1.002 | 5.01 | Smooth
| 5.01.01 | Vertical formwork to
| 5.01.01.01 | Foundations (Floor) | m² | 16
| 5.01.01.02 | Plinths | m² | 9
| 5.01.01.03 | Walls | m² | 375
| 5.01.01.04 | Sump | m² | 4
| 5.01.01.05 | Stairs | m² | 32
| 5.01.02 | Horizontal formwork to
| 5.01.02.01 | Slabs | m² | 80
PSCC1.005 | 5.02 | Narrow widths (up to 300 mm wide)
| 5.02.01 | Vertical Smooth formwork to
| 5.02.01.01 | Precast slabs | m | 105
| 5.02.01.02 | Concrete Bunker Apron Slab | m | 10
PSCC1.006 | 5.03 | Box out holes/form voids
| 5.03.01 | a) Small, circular, of diameter up to 0,35 m
| 5.03.01.01 | 0 m up to and including 0,5 m | No. | 32
| 5.03.02 | d) Large, other than circular, areas over 0.1 m2 up
to 2,0 m2
| 5.03.02.01 | 0 m up to and including 0,5 m | No. | 2
| 5.03.02.02 | Over 2,0 m deep | No. | 7
SCHEDULED REINFORCEMENT ITEMS
| 5.04 | Steel bars
| 5.04.01 | a) Steel bars irrespective of grade and diameter | t | 24
SCHEDULED CONCRETE ITEMS
PSCC1.011 | 5.05 | Blinding layer in Grade 15 MPa/19 mm concrete
| 5.05.01 | 50 mm thickness | m² | 170
Carried forward
Part C - Section 8 - Tie-in chambers: Node NA103, NB12
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.012 | 5.06 | Strength concrete
| 5.06.01 | Class 30 MPa/19 mm concrete in
| 5.06.01.01 | Foundations (Floor) | m3 | 24
| 5.06.01.02 | Plinths | m3 | 6
| 5.06.01.03 | Walls | m3 | 47
| 5.06.01.04 | Roof slab | m3 | 22
| 5.06.01.05 | Sump | m3 | 2
| 5.06.01.06 | Stairs | m3 | 4
| 5.06.01.07 | Concrete Bunker Apron Slab | m3 | 1
PSCC1.013 | 5.07 | Unformed surface finishes
| 5.07.01 | a) Steel-floated finish
| 5.07.01.01 | Foundations (Floor) | m² | 90
| 5.07.01.02 | Top of Plinths | m² | 5
| 5.07.01.03 | Top of Walls | m² | 30
| 5.07.01.04 | Roof slabs | m² | 90
| 5.07.01.05 | Concrete Bunker Apron Slab | m² | 10
| 5.07.02 | d) Broomed finish
| 5.07.02.01 | Blinding layer | m² | 170
| 5.07.03 | e) Screed in 3:1 Sand and Cement Mix
| 5.07.03.01 | Chamber floor screed | m³ | 6
PSCC1.015 | 5.08 | Manufacture (or supply) and erect precast units
| 5.08.01 | Concrete Bunker (Minimum Internal Dimesions: | No. | 1
680 H x 500 W x 375 D)
PSCC1.015 | 5.09 | Joints
| 5.09.01 | Polysulphide sealant between precast slab | m | 50
PSCC1.018 | 5.10 | Grouting
| 5.10.01 | a) Under bases of pipe supports and straps | m³ | 4
| 5.10.02 | c) Pipe box-outs | m³ | 4
Carried forward
Part C - Section 8 - Tie-in chambers: Node NA103, NB12
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.019 | 5.11 | HD bolts and miscellaneous metal work
| 5.11.01 | Metal work for DN 600 Tie-in Chamber 2 as per
Drawing: JW14358-16941-T-013-S26-00-TMS
| 5.11.01.01 | Fabricate and install galvanised mild steel ladders as per Drawing:JW14358-16941-T-017-S09-00-TMS | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.01.02 | Fabricate and cast in long inlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.01.03 | Fabricate and cast in short outlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.01.04 | Fabricate and cast in galvanised access manholes as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.01.05 | Fabricate and cast in lifting hooks as per bolt detail on | No. | 16
Drawing: JW14358-16941-T-017-S10-00-TMS
| 5.11.02 | Metal work for DN 400 Tie-in Chamber as per
Drawing: JW14358-16941-T-013-S35-00-TMS
| 5.11.02.01 | Fabricate and install galvanised mild steel ladders as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.02.02 | Fabricate and cast in long inlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.02.03 | Fabricate and cast in short outlet airvent as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.02.04 | Fabricate and cast in galvanised access manholes as per | No. | 1
Drawing: JW14358-16941-T-017-S09-00-TMS
| 5.11.02.05 | Fabricate and cast in lifting hooks as per bolt detail on | No. | 16
Drawing: JW14358-16941-T-017-S10-00-TMS
PSCC1.020 | 5.12 | Colour Mitigation to:
| 5.12.01 | Exposed Chambers along roadways | m² | 60
MISCELLANEOUS ITEMS
PSCC1.021 | 5.13 | Polythene sheeting under concrete
| 5.13.01 | 250 micron green medium density polyethylene | m² | 170
dampproof sheeting
PSCC1.023 | 5.14 | FRP items
| 5.14.01 | a) FRP Grating
| 5.14.01.01 | 450 mm x 450 mm x 38 mm deep FRP grating | m² | 2
Carried forward
Part C - Section 8 - Tie-in chambers: Node NA103, NB12
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.024 | 5.15 | Casting pipes and specials in concrete
| 5.15.01.01 | DN 200 Steel pipe cast into chamber wall | No. | 1
| 5.15.01.02 | DN 400 Steel pipe cast into chamber wall | No. | 6
PSCC1.025 | 5.16 | Installation of precast elements
| 5.16.01 | Precast roof slabs as per | No. | 4
Drawing: JW14358-16941-T-013-S26-00-TMS
| 5.16.02 | Precast roof slabs as per | No. | 4
Drawing: JW14358-16941-T-013-S35-00-TMS
PSCC1.026 | 5.17 | Drilling cores through concrete
| 5.17.01 | 100 mm diameter core through 250 mm thick concrete | No. | 5
slab
Carried forward to summary (Part C - Section 8)
Part C - Section 8 - Tie-in chambers: Node NA103, NB12
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SUMMARY
SANS 1200 C |  | SITE CLEARANCE
SANS 1200 DB |  | EARTHWORKS (PIPE TRENCHES)
SANS 1200 L |  | MEDIUM-PRESSURE PIPELINES
SANS 1200 LC |  | CABLE DUCTS
SANS 2001 CC1 |  | CONCRETE (STRUCTURAL)
Total carried forward to summary

## Part D-AC&CP
Part D - Portion 1 - Cathodic Protection
Transformer rectifier infrastructure installations
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SECTION A | A | Transformer Rectifier Infrastructure Installations
| A1 | Preliminary & General
| A1.01 | For one Transformer Rectifier Infrastructure Installation - n | Each | 1
to include for all plant, equipment, personnel, site
establishment, travelling, concrete testing by SANAS
accredited laboratory for all concrete mixes, barricading
of trenches dewatering, security for the protection of
Cables left exposed overnight and removal of all excess
and waste materials on completion
| A2 | Supply and Installation of Negative and Monitoring
Cables
| A2.01 | Negative Cable Trench
| A2.01.01 | From the connection point on the pipeline, excavate a
300mm wide, 1m deep trench to the TRU installation
position. Top soil is to be removed and stored separately.
| A2.01.01.01 | a) Excavation of top soil and separate storage | m | 5
| A2.01.01.02 | b) Excavation of main trench | m | 5
| A2.01.01.03 | c) Extra over for un-pickable material | m³ | 1
| A2.01.01.04 | d) Extra over for rock | m³ | 1
| A2.02 | Cable Connections to Pipeline
| A2.02.01 | Remove existing coating to expose an area of sufficient
size to make the necessary cable connections. Cable
connections are to be by thermit welding or pin brazing
as directed by the Project Manager.
| A2.02.01.01 | a) Coating Removal for 3 cable connections | Each | 1
| A2.02.01.02 | b) 35mm² negative cable connections | Each | 2
| A2.02.01.03 | c) 10mm² monitoring cable connection | Each | 1
| A2.03 | Permanent Reference Electrode and Coupon
| A2.03.01 | The coupon is to be attached to the pipeline anywhere
between the 10 o'clock and 2 o'clock positions. The
permanent reference electrode is to be installed at a
position 200mm perpendicularly away from the pipe and
coupon.
| A2.03.01.01 | a) Supply Permanent Reference electrode, coupon | Each | 1
| A2.03.01.02 | b) Install reference electrode and coupon | Each | 1
Carried forward
Part D - Portion 1 - Cathodic Protection
Transformer rectifier infrastructure installations
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| A2.03 | Permanent Reference Electrode and Coupon
| A2.03.01 | The coupon is to be attached to the pipeline anywhere
between the 10 o'clock and 2 o'clock positions. The
permanent reference electrode is to be installed at a
position 200mm perpendicularly away from the pipe and
coupon.
| A2.03.01.01 | a) Supply Permanent Reference electrode, coupon | Each | 1
| A2.03.01.02 | b) Install reference electrode and coupon | Each | 1
| A2.04 | Cables
| A2.04.01 | From the pipeline, negative, reference, coupon and monitor cables are to be installed inside 110mm PVC conduits with long radius bends. Coating of the cable to pipe connection points is to be carried out
| A2.04.01.01 | a) Supply coating material for 3 cable connections | Each | 1
| A2.04.01.02 | b) Supply 110mm PVC Conduit | m | 5
| A2.04.01.03 | c) Supply 35mm² black PVC/PVC negative cable | m | 15
| A2.04.01.04 | d) Supply 10mm² black PVC/PVC monitoring cable | m | 10
| A2.04.01.05 | e) Supply 10mm² black PVC/PVC coupon cable | m | 10
| A2.04.01.06 | f) Supply 10mm² red PVC/PVC reference cable | m | 10
| A2.04.01.07 | g) Install coating material, conduit and cables | Each | 1
| A2.05 | Concrete Encasement
| A2.05.01 | Cable conduits are to sealed at the pipeline end with Denso mastic or equivalent. The entire cable trench is to be filled with 40MPa concrete up to a level 400mm from the trench floor. Where the conduits come up to ground level the vertical portions of the conduits are to be encased in 40MPa concrete such that the minimum coverage at any point is 400mm.
| A2.05.01.01 | a) Concrete Encasement | m | 5
| A2.06 | Backfilling to Natural Ground Level
| A2.06.01 | Once the concrete has set sufficiently in the trench, backfilling is to be carried out in 200mm layers with compaction of each layer being carried out to 90% modified AASHTO. The Separately stored topsoil is to be installed at the surface.
| A2.06.01.01 | a) Backfilling | m | 5
| A3 | Supply and Installation of Power Supply Cable
| A3.01 | Power Supply Cable Trench
| A3.01.01 | From the power supply metering box, excavate a 450mm
wide, 1m deep trench to the TRU installation position.
Top soil is to be removed and stored separately.
| A3.01.01.01 | a) Excavation of top soil and separate storage | m | 50
| A3.01.01.02 | b) Excavation of main trench | m | 50
| A3.01.01.03 | c) Shoring of Trench | m | 50
| A3.01.01.04 | d) Extra over for un-pickable material | m³ | 1
Carried forward
Part D - Portion 1 - Cathodic Protection
Transformer rectifier infrastructure installations
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| A3.01.01.05 | e) Extra over for rock | m³ | 1
| A3.02 | Cable
| A3.02.01 | From the power supply metering box the AC supply cable
is to be installed inside a 110mm PVC conduit with long
radius bends.
| A3.02.01.01 | a) Supply 110mm PVC Conduit | m | 50
| A3.02.01.02 | b) Supply 2 core 16mm² ECC SWA power cable | m | 55
| A3.02.01.03 | c) Install PVC conduit and power cable | Each | 1
| A3.03 | Concrete Encasement
| A3.03.01 | The entire cable trench is to be filled with 40 MPa
concrete up to a level 400mm from the trench floor.
Where the conduits come up to ground level the vertical
portions of the conduits are to be encased in 40 MPa
concrete such that the minimum coverage at any point
is 400 mm
| A3.02.01.01 | a) Concrete Encasement | m | 50
| A3.04 | Backfilling to Natural Ground Level
| A3.04.01 | Once the concrete has set sufficiently in the trench,
backfilling is to be carried out in 200mm layers with
compaction of each layer being carried out to 90%
90% of modified AASHTO density. The separately stored
topsoil is to be installed at the surface.
| A3.02.01.01 | a) Backfilling | m | 50
| A3.05 | Isolator Box
| A3.05.01 | A suitable isolator box, complete with suitably rated
isolator, is to be installed in the secure underground
enclosure. The AC Supply cable is to be terminated
inside this box.
| A3.05.01.01 | a) Supply and Install Isolator | Each | 1
Carried forward
Part D - Portion 1 - Cathodic Protection
Transformer rectifier infrastructure installations
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| A4 | Supply and Installation of Secure Enclosure
| A4.01 | TRU Earthing
| A4.01.01 | Trenches for earthing cables are to be excavated to a
depth of 0.5m. Earthing cables are to be laid as specified
and 1.2m long earth spikes are to be driven in to the earth
at each corner or conductor intersection. At each of these
corners or intersections the conductors and earth rods
are to be thermit welded together. The earthing trenches
are then to be filled with 40 MPa concrete and backfilled.
| A4.01.01.01 | a) Excavation of top soil and separate storage | m | 16
| A4.01.01.02 | b) Excavation of main trench | m | 16
| A4.01.01.03 | c) Extra over for un-pickable material | m³ | 1
| A4.01.01.04 | d) Extra over for rock | m³ | 1
| A4.01.01.05 | e)Earthing Material Supply | Sum | 1
| A4.01.01.06 | f) Earthing Material Installation | Sum | 1
| A4.02 | Backfilling of TRU Earthing
| A4.02.01 | Once the concrete has set sufficiently in the trenches,
backfilling is to be carried out in 200 mm layers with
compaction of each layer being carried out to 90% of
modified AASHTO density.
| A4.02.01.01 | a) Backfilling | Sum | 1
| A4.03 | TRU Secure Enclosure
| A4.03.01 | Secure underground enclosure to be installed as per
manufacturers specifications.
| A4.03.01.01 | a) Supply | Each | 1
| A4.03.01.02 | b) Install | Each | 1
Carried forward to summary (Section A)
Part D - Portion 1 - Cathodic Protection
Supply and installation of transformer rectifier units
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SECTION B | B | Supply and Installation of Transformer Rectifier Units
| B1 | Preliminary & General
| B1.01 | Rate for one Transformer Rectifier Installation (to include | Each | 1
for all plant, equipment, personnel, site establishment,
travelling and security and removal of all excess and
waste materials on completion
| B2 | 3kW SMCPR
| B2.01 | Manufacture and test Unit, carry out FAT in presence of
the Engineer, deliver to site Install and issue COC.
Installation to include the termination of the point of supply
inside the bunker enclosure with a Schneider PM5000
series power meter and CT’s (free issue from JW).
Remote monitoring to be via GSM-GDSP. 40 hours of
development costs to be allowed to ensure the unit is
interfaced with the 24/7/365 SCADA system in the control
room with the appropriate, connectivity, alarming and data
storage in the MS SQL database which is hosted
at Johannesburg Water Head Quarters.
| B2.01.01 | Supply SMCPR | Each | 1
| B2.01.02 | Factory Acceptance Testing of TRU in the presence of | Each | 1
the Supervisor
| B2.01.03 | Install SMCPR | Each | 1
| B2.01.04 | Development costs for SCADA interface | Hours | 40
Carried forward to summary (Section B)
Part D - Portion 1 - Cathodic Protection
Supply and installation of horizontal anode groundbed
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SECTION C | C | Supply and Installation of Horizontal Anode Groundbed
| C1 | Preliminary & General
| C1.01 | For one horizontal anode groundbed Installation - to | Each | 1
include for all plant, equipment, personnel, site
establishment, travelling, concrete testing by SANAS
accredited laboratory for all concrete mixes, barricading
of trenches, dewatering, security for the protection of
cables left exposed overnight and removal of all excess
and waste materials on completion
| C2 | Supply and Installation of Positive Cables
| C2.01 | Positive Cable Trench
| C2.01.01 | From the transformer rectifier enclosure, excavate a
300 mm wide, 1m deep trench to the groundbed
installation position. Top soil is to be removed and stored
separately.
| C2.01.01.01 | a) Excavation of top soil and separate storage | m | 320
| C2.01.01.02 | b) Excavation of main trench | m | 320
| C2.01.01.03 | c) Extra over for un-pickable material | m³ | 1
| C2.01.01.04 | d) Extra over for rock | m³ | 1
| C2.02 | Supply and Installation of Positive Cable
| C2.02.01 | From the furthest end of the anode groundbed cables are
to be installed inside partly the groundbed trench and
partly the positive cable trench. Cables are to be brought
into the TRU enclosure via the cable duct.
| C2.02.01.01 | a) Supply 35mm² red PVC/PVC positive cable | m | 410
| C2.02.01.02 | b) Install 35mm² red PVC/PVC positive cable | m | 410
| C2.03 | Concrete Encasement
| C2.03.01 | The entire positive cable trench is to be filled with 40 MPa
concrete up to a level 400mm from the trench floor.
| C2.03.01.01 | a) Concrete Encasement | m | 320
| C2.04 | Backfilling to Natural Ground Level
| C2.04.01 | Once the concrete has set sufficiently in the trench,
backfilling is to be carried out in 200 mm layers with
compaction of each layer being carried out to 90% of
modified AASHTO density. The separately stored topsoil
is to be installed at the surface.
| C2.04.01.01 | a) Backfilling | m | 320
Carried forward
Part D - Portion 1 - Cathodic Protection
Supply and installation of horizontal anode groundbed
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| C2.05 | Installation of Cable Route Markers
| C2.02.01 | Cable route markers are to be installed at 50 m intervals
and at all direction changes along the cable route.
| C2.02.01.01 | a) Cable route markers | Each | 9
| C3 | Supply and Installation of Anode Groundbed
| C3.01 | Anode Groundbed Trench
| C3.01.01 | At the location indicated by the engineer, excavate a
300 mm wide, 2.5 m deep trench. Top soil is to be
removed and stored separately.
| C3.01.01.01 | a) Excavation of top soil and separate storage | m | 80
| C3.01.01.02 | b) Excavation of main trench | m | 80
| C3.01.01.03 | c) Shoring of Trench | m | 80
| C3.01.01.04 | d) Extra over for un-pickable material | m³ | 1
| C3.01.01.05 | e) Extra over for rock | m³ | 1
| C3.02 | Anodes and Canisters
| C3.02.01 | The anode canisters are to be laid next to the trench
alternately with the spacer canisters. Anode tails are to
be spliced to the ring main cable by means of line taps
and y-type epoxy filled splicing kits. Once the epoxy
has cured sufficiently anode and spacer canisters
are to be lowered carefully into the trench
using appropriate slings.
| C3.02.01.01 | a) Supply canisterised anodes | Each | 20
| C3.02.01.02 | b) Supply spacer canisters | Each | 20
| C3.02.01.03 | c) Supply Splicing kits and line taps | Each | 20
| C3.02.01.04 | d) Install anode groundbed | Each | 1
| C3.03 | Backfilling to Natural Ground Level
| C3.03.01 | Backfilling is to be carried out in 200 mm layers with
compaction of each layer being carried out to 90% of
modified AASHTO density. The separately stored
topsoil is to be installed at the surface.
| C3.03.01.01 | Backfilling | m | 80
Carried forward to summary (Section C)
Part D - Portion 1 - Cathodic Protection
Supply and installation of cross bonds
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SECTION D | D | Supply and Installation of Cross Bonds
| D1 | Preliminary & General
| D2.01 | For one cross bond Installation - to include for all plant, | Each | 1
equipment, personnel, site establishment, travelling,
concrete testing by SANAS accredited laboratory for all
concrete mixes, barricading of trenches dewatering,
security for the protection of cables left exposed overnight
and removal of all excess and waste materials on
completion.
| D2 | Supply and Installation of Cross Bond
| D2.01 | Excavation
| D2.01.01 | At each cross bonding location, excavate a 300mm wide
trench to a depth of 1m or depth of pipeline invert (if
greater than 1m). Top soil is to be removed and stored
separately.
| D2.01.01.01 | a) Excavation of top soil and separate storage | m | 1
| D2.01.01.02 | b) Excavation of main trench | m | 1
| D2.01.01.03 | c) Shoring of Trench | m | 1
| D2.01.01.04 | d) Extra over for un-pickable material | m³ | 1
| D2.01.01.05 | e) Extra over for rock | m³ | 1
| D2.02 | Cable Connections to Pipeline
| D2.02.01 | Remove existing coating to expose an area of sufficient
size to make the necessary cable connections. Cable
connections are to be by thermit welding.
| D2.02.01.02 | a) Coating Removal for 4 cable connections | Each | 1
| D2.03 | Cables
| D2.03.01 | Cross bonding cables are to be laid between the pipelines
Coating of the cable to pipe connection points is to be
carried out. Cable terminations are to be made at a
4-way link panel housed in a below ground monitoring
enclosure.
| D2.03.01.01 | a) Supply coating material for 4 cable connections | Each | 1
| D2.03.01.02 | b) Supply 35mm² black PVC/PVC negative cable | m | 1210
| D2.03.01.03 | c) Install coating material and cables | Each | 1
| D2.03.01.04 | d) Supply 4 way link panel | Each | 1
| D2.03.01.05 | e) Install 4 way link panel | Each | 1
Carried forward
Part D - Portion 1 - Cathodic Protection
Supply and installation of cross bonds
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| D2.04 | Concrete Encasement
| D2.04.01 | Trenches are to be filled with 400 mm of 40 MPa
concrete and the cable completely encased.
| D2.04.01.01 | a) Concrete Encasement | m | 600
| D2.05 | Backfilling to Natural Ground Level
| D2.05.01 | In each trench, backfilling is to be carried out in 200 mm
layers with compaction of each layer being carried out to
90% of modified AASHTO density. The separately stored
topsoil is to be reinstated at the surface.
| D2.05.01.01 | a) Backfilling | m | 600
Carried forward to summary (Section D)
Part D - Portion 1 - Cathodic Protection
Supply and installation of continuity bonds at chambers
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SECTION E | E | Supply and Installation of Continuity Bonds at
Chambers
| E1 | Preliminary & General
| E1.01 | For one chamber continuity bond Installation - to include | Each | 23
for all plant, equipment, personnel, site establishment,
travelling, concrete testing by SANAS accredited
laboratory for all concrete mixes, barricading of trenches
dewatering, security for the protection of cables left
exposed overnight and removal of all excess and waste
materials on completion
| E2 | Supply and Installation of Chamber Continuity Bond
| E2.01 | Excavation
| E2.01.01 | At each chamber requiring bonding, excavate a 300 mm
wide trench to a depth of 1 m or depth of pipeline invert
(if greater than 1 m) around the chamber immediately
adjacent to the chamber wall. Top soil is to be removed
and stored separately.
| E2.01.01.01 | a) Excavation of top soil and separate storage | m | 115
| E2.01.01.02 | b) Excavation of main trench | m | 115
| E2.01.01.03 | c) Shoring of Trench | m | 115
| E2.01.01.04 | d) Extra over for un-pickable material | m³ | 1
| E2.01.01.05 | e) Extra over for rock | m³ | 1
| E2.02 | Cable Connections to Pipeline
| E2.02.01 | Remove existing coating to expose an area of sufficient
size to make the necessary cable connections. Cable
connections are to be by thermit welding.
| E2.02.01.01 | a) Coating Removal for 4 cable connections | Each | 184
| E2.02.01.02 | b) 35mm² bonding cable connections | Each | 92
| E2.03 | Cables
| E2.03.01 | Continuity bonding cables are to be laid around each
chamber. Coating of the cable to pipe connection points
is to be carried out.
| E2.03.01.01 | a) Supply coating material for cable connections | Each | 92
| E2.03.01.02 | b) Supply 35mm² black PVC/PVC negative cable | Each | 276
| E2.03.01.03 | c) Install coating material and cables | Each | 23
Carried forward
Part D - Portion 1 - Cathodic Protection
Supply and installation of continuity bonds at chambers
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| E2.04 | Concrete Encasement
| E2.04.01 | Trenches are to be filled with 400 mm of 40M Pa
concrete and the cable completely encased.
| E2.04.01.01 | a) Concrete Encasement | m | 115
| E2.05 | Backfilling to Natural Ground Level
| E2.05.01 | In each trench, backfilling is to be carried out in 200 mm
layers with compaction of each layer being carried out to
90% of modified AASHTO density. The separately stored
topsoil is to be reinstated at the surface.
| E2.05.01.01 | a) Backfilling | m | 115
Carried forward to summary (Section E)
Part D - Portion 1 - Cathodic Protection
Supply and installation of monitoring facilities
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SECTION F | F | Supply and Installation of Monitoring Facilities
| F1 | Preliminary & General
| F1.01 | For one Monitoring Facility Installation - to include for all | Each | 9
plant, equipment, personnel, site establishment, travelling,
concrete mixes, barricading of trenches dewatering,
concrete testing by SANAS accredited laboratory for all
security for the protection of cables left exposed overnight
and removal of all excess and waste materials on
completion.
| F2 | Supply and Installation of Monitoring Facility -
Below Ground Type
| F2.01 | Monitoring Cable Trench
| F2.01.01 | At the designated point on each of the pipelines, excavate
to the pipe overt and then excavate a 300 mm wide, 1 m
deep trench to the monitoring enclosure installation
position. Top soil is to be removed and stored separately.
| F2.01.01.01 | a) Excavation of top soil and separate storage | m | 21
| F2.01.01.02 | b) Excavation of main trench | m | 21
| F2.01.01.03 | c) Shoring of Trench | m | 21
| F2.01.01.04 | d) Extra over for un-pickable material | m³ | 1
| F2.01.01.05 | e) Extra over for rock | m³ | 1
| F2.02 | Cable Connections to Pipeline
| F2.02.01 | Remove existing coating to expose an area of sufficient
size to make the necessary cable connections. Cable
connections are to be by thermit welding.
| F2.02.01.01 | a) Coating Removal for 1 cable connections | Each | 7
| F2.02.01.02 | b) 10mm² monitoring cable connection | Each | 7
Carried forward
Part D - Portion 1 - Cathodic Protection
Supply and installation of monitoring facilities
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| F2.03 | Permanent Reference Electrode and Coupon
| F2.03.01 | The coupon is to be attached to the pipeline anywhere
between the 10 o'clock and 2 o'clock positions. The
permanent reference electrode is to be installed at a
position 200 mm perpendicularly away from the pipe and
coupon.
| F2.03.01.01 | a) Supply Permanent Reference electrode, coupon. | Each | 7
| F2.03.01.02 | b) Install reference electrode and coupon | Each | 7
| F2.04 | Cables
| F2.04.01 | From the pipeline, the reference, coupon and monitor
cables are to be installed inside 110 mm PVC conduits
long radius bends. Coating of the cable to pipe connection
with points is to be carried out.
| F2.04.01.01 | a) Supply coating material for cable connections | Each | 7
| F2.04.01.02 | b) Supply 10mm² black PVC/PVC monitoring cable | m | 35
| F2.04.01.03 | c) Supply 10mm² black PVC/PVC coupon cable | m | 35
| F2.04.01.04 | d) Supply 10mm² red PVC/PVC reference cable | m | 35
| F2.04.01.05 | e) Install coating material, permanent reference | Each | 7
electrodes and cables
| F2.05 | Concrete Encasement
| F2.05.01 | The entire cable trench is to be filled with 40 MPa
concrete up to a level 400mm from the trench floor.
| F2.05.01.01 | a) Concrete Encasement | m | 21
| F2.06 | Backfilling to Natural Ground Level
| F2.06.01 | Once the concrete has set sufficiently in the trench,
backfilling is to be carried out in 200 mm layers with
compaction of each layer being carried out to 90% of
modified AASHTO density. The separately stored topsoil
is to be installed at the surface.
| F2.06.01.01 | a) Backfilling | m | 21
| F2.07 | Monitoring Enclosure
| F2.07.01 | Supply and Install Monitoring Enclosure (Including
concrete encasement)
| F2.07.01.01 | a) Supply Monitoring Enclosure | Each | 7
| F2.07.01.02 | a) Install Monitoring Enclosure | Each | 7
Carried forward
Part D - Portion 1 - Cathodic Protection
Supply and installation of monitoring facilities
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| F3 | Supply and Installation of Monitoring Facility -
Big Head Test Post Type
| F3.01 | Monitoring Cable Trench
| F3.01.01 | At the designated point on each of the pipelines, excavate
to the pipe overt and then excavate a 300 mm wide, 1 m
deep trench to the monitoring enclosure installation
position. Top soil is to be removed and stored separately.
| F3.01.01.01 | a) Excavation of top soil and separate storage | m | 6
| F3.01.01.02 | b) Excavation of main trench | m | 6
| F3.01.01.03 | c) Shoring of Trench | m | 6
| F3.01.01.04 | d) Extra over for un-pickable material | m³ | 1
| F3.01.01.05 | e) Extra over for rock | m³ | 1
| F3.02 | Cable Connections to Pipeline
| F3.02.01 | Remove existing coating to expose an area of sufficient
size to make the necessary cable connections. Cable
connections are to be by thermit welding.
| F3.02.01.01 | a) Coating Removal for 1 cable connections | m | 6
| F3.02.01.02 | b) 10mm² monitoring cable connection | m | 6
| F3.03 | Permanent Reference Electrode and Coupon
| F3.03.01 | The coupon is to be attached to the pipeline anywhere
between the 10 o'clock and 2 o'clock positions. The
permanent reference electrode is to be installed at a
position 200 mm perpendicularly away from the pipe
and coupon.
| F3.03.01.01 | a) Supply Permanent Reference electrode, coupon | Each | 2
| F3.03.01.02 | b) Install reference electrode and coupon | Each | 2
Carried forward
Part D - Portion 1 - Cathodic Protection
Supply and installation of monitoring facilities
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| F3.04 | Cables
| F3.04.01 | From the pipeline, the reference, coupon and monitor
cables are to be installed inside 110mm PVC conduits
with long radius bends. Coating of the cable to pipe
connection points is to be carried out.
| F3.04.01.01 | a) Supply coating material for cable connections | Each | 2
| F3.04.01.02 | b) Supply 10mm² black PVC/PVC monitoring cable | m | 10
| F3.04.01.03 | c) Supply 10mm² black PVC/PVC coupon cable | m | 10
| F3.04.01.04 | d) Supply 10mm² red PVC/PVC reference cable | m | 10
| F3.04.01.05 | e) Install coating material, permanent reference | Each | 2
electrodes and cables
| F3.05 | Concrete Encasement
| F3.05.01 | The entire cable trench is to be filled with 40 MPa
concrete up to a level 400 mm from the trench floor.
| F3.05.01.01 | a) Concrete Encasement | m | 6
| F3.06 | Backfilling to Natural Ground Level
| F3.06.01 | Once the concrete has set sufficiently in the trench,
backfilling is to be carried out in 200 mm layers with
compaction of each layer being carried out to 90% of
modified AASHTO density. The separately stored topsoil
is to be installed at the surface.
| F3.06.01.01 | a) Backfilling | m | 6
| F3.07 | Monitoring Enclosure
| F3.07.01 | Supply and Install Monitoring Enclosure (Including
concrete foundation and surround)
| F3.07.01.01 | a) Supply Monitoring Enclosure | Each | 2
| F3.07.01.02 | b) Install Monitoring Enclosure | Each | 2
Carried forward to summary (Section F)
Part D - Portion 1 - Cathodic Protection
Supply and installation of gradient control mats (large chambers)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SECTION G | G | Supply and Installation of Gradient Control Mats
(Large Chambers)
| G1 | Preliminary & General
| G1.01 | For one gradient control mat Installation - to include for all | Each | 2
plant, equipment, personnel, site establishment, travelling,
concrete testing by SANAS accredited laboratory for all
concrete mixes, barricading of trenches dewatering,
security for the protection of cables left exposed overnight
and removal of all excess and waste materials on
completion.
| G2 | Supply and Installation of Gradient Control Mat
| G2.01 | Excavation for GCM Installation
| G2.01.01 | At the designated valve chamber, excavate to the pipe at
a point immediately adjacent to the chamber wall to make
the cable connection to the pipe, excavate further to the
level of the chamber floor to receive the GCM cables
from the internal mat. Once the cables have been brought
up to ground level, backfill and compact the excavation to
a depth of 0.5 m below natural ground level. Excavate an
area 1.2m wide around the chamber to a depth of
0.5m.Top soil is to be removed and stored separately.
| G2.01.01.01 | a) Excavation of top soil and separate storage | Sum | 2
| G2.01.01.02 | b) Excavation of main trench | Sum | 2
| G2.01.01.03 | c) Extra over for un-pickable material | m³ | 1
| G2.01.01.04 | d) Extra over for rock | m³ | 1
| G2.02 | Cable Connections to Pipeline
| G2.01.01 | Remove existing coating to expose an area of sufficient
size to make the necessary cable connections. Cable
connections are to be by thermit welding.
| G2.01.01.01 | a) Coating Removal for 2 cable connections | Each | 2
| G2.01.01.02 | b) 70mm² GCM pipe cable connection | Each | 2
Carried forward
Part D - Portion 1 - Cathodic Protection
Supply and installation of gradient control mats (large chambers)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| G2.03 | Cables
From the pipeline, the internal GCM and the external
GCM the pipe connection and GCM connection cables are
to be brought to a point 100 mm below the level of the
external GCM. At this position the GCM cables are to be
connected to two M10 stainless steel rods which are
inserted through the wall c/w insulating sleeves and
washers. Connection of the cables to the threaded rods is
to be by means of lugs, nuts and washers. Coating of the
cable to pipe connection as well as the cable to M10 rod
connection is to be carried out. The latter is to be carried
out using Stopaq or equivalent.
| G2.03.01.01 | a) Supply coating material for cable connections | Each | 2
| G2.03.01.02 | b) 70mm² GCM pipe cable connection | Each | 4
| G2.03.01.03 | c) Supply 70mm² black PVC/PVC pipe cable | m | 8
| G2.03.01.04 | d) Supply 70mm² green PVC/PVC GCM cables | m | 16
| G2.03.01.05 | e) Install coating material, insulated rods and cables | Each | 2
| G2.04 | Internal Gradient Control Mat
| G2.04.01 | The chamber floor is to be cleaned manually and then
washed with a high pressure washer. The 100x100x4 mm
hot dip galvanized weld mesh is to be laid flat on the
chamber floor such that the entire floor is covered with
the exception of any drainage holes pipe support bases
etc. The weld mesh is to be cut at least 50 mm clear of
any steel work attached to the chamber floor. Any joints
between segments of weld mesh are to be made using
thermit welds as are the two 70 mm² cable connections.
These joints are to be wrapped with Stopaq or equivalent.
The two 70 mm² cables are to exit through the chamber
wall no more than 25 mm above floor level. The entire
weld mesh as well as the cables is to be covered with
75 mm of 40 MPa concrete. Should the chamber have
any drains, the concrete should be floated to fall toward
the drains at the same angle as the original floor.
| G2.04.01.01 | a) Supply galvanised weld mesh | Sum | 2
| G2.04.01.02 | b) Supply coating material for cable and mesh | Sum | 2
connections
| G2.04.01.03 | c) Supply thermit weld connections for GCM cables and | Sum | 2
mesh joints
| G2.04.01.04 | d) Install GCM, thermit weld connections and cables | Each | 2
| G2.04.01.05 | e) Supply and Install 75mm concrete cover of mesh | Sum | 2
and cables
Carried forward
Part D - Portion 1 - Cathodic Protection
Supply and installation of gradient control mats (large chambers)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| G2.05 | External Gradient Control Mat
| G2.05.01 | The floor of the GCM excavation is to be even, level and
compacted. The 100x100x4 mm hot dip galvanized weld
mesh is to be laid flat on the excavation floor such that the
entire floor is covered and a 1.2 m wide border of mesh is
formed around the chamber wall. Any joints between
segments of weld mesh are to be made using thermit
welds as are the two 70 mm² cable connections. These
joints are to be wrapped with Stopaq or equivalent. The
entire weld mesh as well as the cables is to be covered
with 200 mm of 40 MPa concrete.
| G2.05.01.01 | a) Supply galvanised weld mesh including sacrificial anodes | Sum | 2
| G2.05.01.02 | b) Supply coating material for cable and mesh connections | Sum | 2
| G2.05.01.03 | c) Supply thermit weld connections for GCM cables and | Sum | 2
mesh joints
| G2.05.01.04 | d) Install GCM, thermit weld connections and cables | Each | 2
| G2.05.01.05 | e) Supply and Install 200mm concrete cover of mesh | Sum | 2
| G2.06 | Backfilling to Natural Ground Level
| G2.06.01 | Once the concrete has set sufficiently in the trench, h is
backfilling is to be carried out in 200 mm layers wit
compaction of each layer being carried out to 90% of
modified AASHTO density. The separately stored topsoil
to be installed at the surface.
| G2.06.01.01 | a) Backfilling | Sum | 2
| G2.07 | Solid State Decoupler
| G2.07.01 | Solid state decoupler to be installed inside the valve
chamber immediately adjacent to the connection studs
| G2.07.01.01 | a) Supply SSD | Each | 2
| G2.07.01.02 | b) Install SSD | Each | 2
Carried forward to summary (Section G)
Part D - Portion 1 - Cathodic Protection
Supply and installation of gradient control mats (medium chambers)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SECTION H | H | Supply and Installation of Gradient Control Mats
(Medium Chambers)
| H1 | Preliminary & General
| H1.01 | For one gradient control mat Installation - to include for all | Each | 6
plant, equipment, personnel, site establishment, travelling,
concrete testing by SANAS accredited laboratory for all
concrete mixes, barricading of trenches dewatering,
security for the protection of cables left exposed overnight
and removal of all excess and waste materials on
completion.
| H2 | Supply and Installation of Gradient Control Mat
| H2.01 | Excavation for GCM Installation
| H2.01.01 | At the designated valve chamber, excavate to the pipe at
a point immediately adjacent to the chamber wall to make
the cable connection to the pipe, excavate further to the
level of the chamber floor to receive the GCM cables
from the internal mat. Once the cables have been brought
up to ground level, backfill and compact the excavation to
a depth of 0.5 m below natural ground level. Excavate an
area 1.2 m wide around the chamber to a depth of
0.5 m.Top soil is to be removed and stored separately.
| H2.01.01.01 | a) Excavation of top soil and separate storage | Sum | 6
| H2.01.01.02 | b) Excavation of main trench | Sum | 6
| H2.01.01.03 | c) Extra over for un-pickable material | m³ | 6
| H2.01.01.04 | d) Extra over for rock | m³ | 6
| H2.02 | Cable Connections to Pipeline
| H2.02.01 | Remove existing coating to expose an area of sufficient
size to make the necessary cable connections. Cable
connections are to be by thermit welding.
| H2.02.01.01 | a) Coating Removal for 2 cable connections | Each | 6
| H2.02.01.02 | b) 70mm² GCM pipe cable connection | Each | 12
Carried forward
Part D - Portion 1 - Cathodic Protection
Supply and installation of gradient control mats (medium chambers)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| H2.03 | Cables
| H2.03.01 | From the pipeline, the internal GCM and the external
GCM the pipe connection and GCM connection cables
are to be brought to a point 100 mm below the level of
the external GCM. At this position the GCM cables are to
be connected to two M10 stainless steel rods which are
inserted through the wall c/w insulating sleeves and
washers. Connection of the cables to the threaded rods is
to be by means of lugs, nuts and washers. Coating of the
cable to pipe connection as well as the cable to M10 rod
connection is to be carried out. The latter is to be carried
out using Stopaq or equivalent.
| H2.03.01.01 | a) Supply coating material for cable connections | Each | 6
| H2.03.01.02 | b) Supply insulated stainless steel threaded rods | Each | 12
| H2.03.01.03 | c) Supply 70mm² black PVC/PVC pipe cable | m | 24
| H2.03.01.04 | d) Supply 70mm² green PVC/PVC GCM cables | m | 48
| H2.03.01.05 | e) 70mm² GCM pipe cable connection | Each | 6
| H2.04 | Internal Gradient Control Mat
| H2.04.01 | The chamber floor is to be cleaned manually and then
washed with a high pressure washer. The 100x100x4 mm
hot-dip galvanized weld mesh is to be laid flat on the
chamber floor such that the entire floor is covered with
the exception of any drainage holes pipe support bases
etc. The weld mesh is to be cut at least 50 mm clear of
any steel work attached to the chamber floor. Any joints
between segments of weld mesh are to be made using
thermit welds as are the two 70 mm² cable connections.
These joints are to be wrapped with Stopaq or equivalent.
The two 70 mm² cables are to exit through the chamber
wall no more than 25 mm above floor level. The entire
weld mesh as well as the cables is to be covered with
75 mm of 40 MPa concrete. Should the chamber have
any drains, the concrete should be floated to fall toward
the drains at the same angle as the original floor.
| H2.04.01.01 | a) Supply galvanised weld mesh | Sum | 6
| H2.04.01.02 | b) Supply coating material for cable and mesh connections | Sum | 6
| H2.04.01.03 | c) Supply thermit weld connections for GCM cables and | Sum | 6
mesh joints
| H2.04.01.04 | d) Install GCM, thermit weld connections and cables | Each | 6
| H2.04.01.05 | e) Supply and Install 75mm concrete cover of mesh and | Sum | 6
Carried forward
Part D - Portion 1 - Cathodic Protection
Supply and installation of gradient control mats (medium chambers)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| H2.05 | External Gradient Control Mat
| H2.05.01 | The floor of the GCM excavation is to be even, level and
compacted. The 100x100x4 mm hot dip galvanized weld
mesh is to be laid flat on the excavation floor such that the
entire floor is covered and a 1.2 m wide border of mesh is
formed around the chamber wall. Any joints between
segments of weld mesh are to be made using thermit
welds as are the two 70 mm² cable connections. These
joints are to be wrapped with Stopaq or equivalent. The
entire weld mesh as well as the cables is to be covered
with 200 mm of 40 MPa concrete.
| H2.05.01.01 | a) Supply galvanised weld mesh including sacrificial | Sum | 6
anodes
| H2.05.01.02 | b) Supply coating material for cable and mesh | Sum | 6
connections
| H2.05.01.03 | c) Supply thermit weld connections for GCM cables and | Sum | 6
mesh joints
| H2.05.01.04 | d) Install GCM, thermit weld connections and cables | Each | 6
| H2.05.01.05 | e) Supply and Install 75 mm concrete cover of mesh | Sum | 6
and cables
| H2.06 | Backfilling to Natural Ground Level
| H2.06.01 | Once the concrete has set sufficiently in the trench,
backfilling is to be carried out in 200 mm layers with
compaction of each layer being carried out to 90% of
modified AASHTO density. The separately stored topsoil
is to be reinstated at the surface.
| H2.06.01.01 | a) Backfilling | Sum | 6
| H2.07 | Solid State Decoupler
| H2.07.01 | Solid state decoupler to be installed inside the valve
chamber immediately adjacent to the connection studs
| H2.07.01.01 | a) Supply SSD | Each | 6
| H2.07.01.02 | b) Install SSD | Each | 6
Carried forward to summary (Section H)
Part D - Portion 1 - Cathodic Protection
Supply and installation of gradient control mats (air valve chamber)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SECTION I | I | Supply and Installation of Gradient Control Mats
(Air Valve Chamber)
| I1 | Preliminary & General
| I1.01 | For one gradient control mat Installation - to include for all | Each | 15
plant, equipment, personnel, site establishment, travelling,
concrete testing by SANAS accredited laboratory for all
concrete mixes, barricading of trenches dewatering,
security for the protection of cables left exposed overnight
and removal of all excess and waste materials on
completion.
| I2 | Supply and Installation of Gradient Control Mat
| I2.01 | Excavation for GCM Installation
| I2.01.01 | At the designated valve chamber, excavate to the pipe at
a point immediately adjacent to the chamber wall to make
the cable connection to the pipe, excavate further to the
level of the chamber floor to receive the GCM cables from
the internal mat. Once the cables have been brought up to
ground level, backfill and compact the excavation to a
depth of 0.5 m below natural ground level. Excavate an
area 1.2 m wide around the chamber to a depth of
0.5 m. Top soil is to be removed and stored separately.
| I2.01.01.01 | a) Excavation of top soil and separate storage | Sum | 15
| I2.01.01.02 | b) Excavation of main trench | Sum | 15
| I2.01.01.03 | c) Extra over for un-pickable material | m³ | 15
| I2.01.01.04 | d) Extra over for rock | m³ | 15
| I2.02 | Cable Connections to Pipeline
| I2.02.01 | Remove existing coating to expose an area of sufficient
size to make the necessary cable connections. Cable
connections are to be by thermit welding.
| I2.02.01.01 | a) Coating Removal for 2 cable connections | Each | 15
| I2.02.01.02 | b) 70mm² GCM pipe cable connection | Each | 30
Carried forward
Part D - Portion 1 - Cathodic Protection
Supply and installation of gradient control mats (air valve chamber)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| I2.03 | Cables
| I2.03.01 | From the pipeline, the internal GCM and the external
GCM the pipe connection and GCM connection cables are
to be brought to a point 100 mm below the level of the
external GCM. At this position the GCM cables are to be
connected to two M10 stainless steel rods which are
inserted through the wall c/w insulating sleeves and
washers. Connection of the cables to the threaded rods is
to be by means of lugs, nuts and washers. Coating of the
cable to pipe connection as well as the cable to M10 rod
connection is to be carried out. The latter is to be carried
out using Stopaq or equivalent.
| I2.03.01.01 | a) Supply coating material for cable connections | Each | 15
| I2.03.01.02 | b) Supply insulated stainless steel threaded rods | Each | 30
| I2.03.01.03 | c) Supply 70mm² black PVC/PVC pipe cable | m | 60
| I2.03.01.04 | d) Supply 70mm² green PVC/PVC GCM cables | m | 90
| I2.03.01.05 | e) Install coating material, insulated rods and cables | Each | 15
| I2.04 | Internal Gradient Control Mat
| I2.04.01 | The crushed stone is to be removed from the chamber
floor. The 100x100x4 mm hot dip galvanized weld mesh is
to be laid flat on the chamber floor such that the entire
floor is covered. The weld mesh is to be cut at least
50 mm clear of any steel work. Any joints between
segments of weld mesh are to be made using thermit
welds as are the two 70 mm² cable connections. These
joints are to be wrapped with Stopaq or equivalent. The
two 70 mm² cables are to exit through the chamber wall
no more than 25 mm above floor level. The entire weld
mesh as well as the cables is to be covered with 75 mm
of 40 MPa concrete. The crushed stone is then to be
replaced inside the chamber.
| I2.04.01.01 | a) Supply galvanised weld mesh | Sum | 15
| I2.04.01.02 | b) Supply coating material for cable and mesh connections | Sum | 15
| I2.04.01.03 | c) Supply thermit weld connections for GCM cables and | Sum | 15
mesh joints
| I2.04.01.04 | d) Install GCM, thermit weld connections and cables | Each | 15
| I2.04.01.05 | e) Supply and Install 75mm concrete cover of mesh and | Sum | 15
cables
Carried forward
Part D - Portion 1 - Cathodic Protection
Supply and installation of gradient control mats (air valve chamber)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| I2.05 | External Gradient Control Mat
| I2.05.01 | The floor of the GCM excavation is to be even, level and
compacted. The 100x100x4 mm hot dip galvanized weld
mesh is to be laid flat on the excavation floor such that the
entire floor is covered and a 1.2 m wide border of mesh is
formed around the chamber wall. Any joints between
segments of weld mesh are to be made using thermit
welds as are the two 70 mm² cable connections. These
joints are to be wrapped with Stopaq or equivalent. The
entire weld mesh as well as the cables is to be covered
with 200 mm of 40 MPa concrete.
| I2.05.01.01 | a) Supply galvanised weld mesh | Sum | 15
| I2.05.01.02 | b) Supply coating material for cable and mesh connections | Sum | 15
| I2.05.01.03 | c) Supply thermit weld connections for GCM cables and | Sum | 15
mesh joints
| I2.05.01.04 | d) Install GCM, thermit weld connections and cables | Each | 15
| I2.05.01.05 | e) Supply and Install 200mm concrete cover of mesh and | Sum | 15
cables
| I2.06 | Backfilling to Natural Ground Level
| I2.06.01 | Once the concrete has set sufficiently in the trench,
backfilling is to be carried out in 200 mm layers with
compaction of each layer being carried out to 90% of
modified AASHTO density. The separately stored topsoil
is to be reinstated at the surface.
| I2.06.01.01 | a) Backfilling | m | 45
| I2.07 | Solid State Decoupler
| I2.07.01 | Solid state decoupler to be installed inside the valve
chamber immediately adjacent to the connection studs .
| I2.07.01.01 | a) Supply SSD | Each | 15
| I2.07.01.02 | b) Install SSD | Each | 15
Carried forward to summary (Section I)
Part D - Portion 1 - Cathodic Protection
Insulating flange kits
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SECTION J | J | Insulating Flange Kits
| J1 | DN600 Bypass
| J1.01 | P&G's for one insulating flange installation (to include for | Each | 1
all plant, equipment, personnel, site establishment,
travelling, dewatering, security and removal of all excess
and waste materials) on completion.
| J1.02 | Supply and Install Bolts, Sleeves, Washers
| J1.02.01 | At the designated location, supply and install bolts,
sleeves and washers
| J1.01.01.01 | a) Supply | Set | 1
| J1.01.01.02 | b) Install | Set | 1
| J1.03 | Supply and Install Gaskets
| J1.03.01 | At the designated location, supply and install bolts,
sleeves and washers
| J1.03.01.01 | a) Supply | Set | 1
| J1.03.01.02 | b) Install | Set | 1
| J2 | DN600 Main
| J2.01 | P&G's for one insulating flange installation (to include for | Each | 1
all plant, equipment, personnel, site establishment,
travelling, dewatering, security and removal of all excess
and waste materials) on completion.
| J2.02 | Supply and Install Bolts, Sleeves, Washers
| J2.02.01 | At the designated location, supply and install bolts,
sleeves and washers
| J2.02.01.01 | a) Supply | Set | 1
| J2.02.01.02 | b) Install | Set | 1
| J2.03 | Supply and Install Gaskets
| J2.03.01 | At the designated location, supply and install bolts,
sleeves and washers
| J2.03.01.01 | a) Supply | Set | 1
| J2.03.01.02 | b) Install | Set | 1
Carried forward
Part D - Portion 1 - Cathodic Protection
Insulating flange kits
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
| J3 | DN800
| J3.01 | P&G's for one insulating flange installation (to include for | Each | 1
all plant, equipment, personnel, site establishment,
travelling, dewatering, security and removal of all excess
and waste materials) on completion.
| J3.02 | Supply and Install Bolts, Sleeves, Washers
| J3.02.01 | At the designated location, supply and install bolts,
sleeves and washers
| J3.02.01.01 | a) Supply | Set | 1
| J3.021.01.02 | b) Install | Set | 1
| J3.03 | Supply and Install Gaskets
| J3.03.01 | At the designated location, supply and install bolts,
sleeves and washers
| J3.03.01.01 | a) Supply | Set | 1
| J3.03.01.02 | b) Install | Set | 1
Carried forward to summary (Section J)
Part D - Portion 1 - Cathodic Protection
Insulating flange kits
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SECTION K | K | Other Items
| K1 | Road Crossings
| K1.01 | At each road crossing a 110 mm diameter cable sleeve is | Each | 9
to be installed by means of horizontal directional drilling at
a depth of 1.5 m
| K2 | Reinstatement of Paving
| K2.01 | Paving to be reinstated to original condition | m² | 100
| K3 | Reinstatement of lawn
| K3.01 | Lawn to be reinstated to original condition
| K3.01.01 | Install | m² | 100
Carried forward to summary (Section K)
Part D - Portion 1 - Cathodic Protection
Summary
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SUMMARY
SECTION A |  | Transformer Rectifier Infrastructure Installations
SECTION B |  | Supply and Installation of Transformer Rectifier Units
SECTION C |  | Supply and Installation of Horizontal Anode Groundbed
SECTION D |  | Supply and Installation of Cross Bonds
SECTION E |  | Supply and Installation of Continuity Bonds at Chambers
SECTION F |  | Supply and Installation of Monitoring Facilities
SECTION G |  | Supply and Installation of Gradient Control Mats (Large Chambers)
SECTION H |  | Supply and Installation of Gradient Control Mats (Medium Chambers)
SECTION I |  | Supply and Installation of Gradient Control Mats (Air Valve Chamber)
SECTION J |  | Insulating Flange Kits
SECTION K |  | Other Items
Total carried forward to summary | [5 empty] | 0

## Trenchless Piping
Part E - Section 1 - Trenchless Piping
Pipe jacking
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 LG | 1 | PIPE JACKING
Refer to Drawing:
JW41358-16941-T-017-S11-00-TMS
8.2.1 | 1.01 | Jacking Establishment
| 1.01.01 | a) Fixed charges
| 1.01.01.01 | Over Marlboro Drive, from Lilium Ave to South Rd, | sum | 1
Marlboro Gardens
| 1.01.01.02 | Over Woodlands Drive via R55 (Woodmead drive), | sum | 1
Woodmead
| 1.01.01.03 | Over South Road, adjacent to Impala road, Marlboro | sum | 1
Gardens
| 1.01.02 | b) Time-related charges
| 1.01.02.01 | Over Marlboro Drive, from Lilium Ave to South Rd, | sum | 1
Marlboro Gardens
| 1.01.02.02 | Over Woodlands Drive via R55 (Woodmead drive), | sum | 1
Woodmead
| 1.01.02.03 | Over South Road, adjacent to Impala road, Marlboro | sum | 1
Gardens
8.2.2 | 1.02 | Supply of pipes to be Jacked
| 1.02.01 | DN 1800 mm Class 100D In-The-Wall Joint pre-cast
concrete jacking pipes (Rocla or similar approved)
| 1.02.01.01 | Over Marlboro Drive, from Lilium Ave to South Rd, | m | 75
Marlboro Gardens
| 1.02.01.02 | Over Woodlands Drive via R55 (Woodmead drive), | m | 40
Woodmead
| 1.02.01.03 | Over South Road, adjacent to Impala road, Marlboro | m | 40
Gardens
8.2.3 | 1.03 | Jacking of pipes
| 1.03.01 | DN 1800 mm Class 100D In-The-Wall Joint pre-cast
concrete jacking pipes (Rocla or similar approved)
| 1.03.01.01 | Over Marlboro Drive, from Lilium Ave to South Rd, | m | 75
Marlboro Gardens
| 1.03.01.02 | Over Woodlands Drive via R55 (Woodmead drive), | m | 40
Woodmead
| 1.03.01.03 | Over South Road, adjacent to Impala road, Marlboro | m | 40
Gardens
Carried forward
Part E - Section 1 - Trenchless Piping
Pipe jacking
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
8.2.4 | 1.04 | Excavation for pipe jacking
| 1.04.01 | Soft excavation | m³ | 233
| 1.04.02 | Intermediate excavation | m³ | 53
| 1.04.03 | Hard rock excavation | m³ | 53
8.2.5 | 1.05 | Extra over items 1.01 and 1.0.4 for unforeseen rock | Stated Sum | 1 | 300000 | 300000
or boulders (Provisional)
8.2.9 | 1.06 | Stabilization of Unstable Areas or Grouting of Voids
where Ordered
| 1.06.01 | a) Provision and establishment of equipment on Site, and | Sum | 1
removal on completion of operation
| 1.06.02 | b) Operation of equipment | Day | 24
| 1.06.03 | c) Materials used | m³ | 100
8.2.10 | 1.07 | Standing time for pipe jacking gang and the jacking | h | 40
equipment covered by item 1.01
Carried forward to summary (Part E - Section 1)
Part E - Section 1 - Trenchless Piping
Medium-pressure pipelines
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 L | 2 | MEDIUM-PRESSURE PIPELINES
PSL 8.2.25 | 2.01 | Supply and Installation of pipe through Horizontal
Direction Drilling (HDD)
| 2.01.01 | PN16 PE100 HDPE
| 2.01.01.01 | DN 200 | m | 200
| 2.01.01.02 | DN 250 | m | 300
PSL 8.2.26 | 2.02 | Laboratory testing of HDPE joints | P.Sum | 1 | 100000 | 100000
Carried forward to summary (Part E - Section 1)
Part E - Portion 1 - Trenchless Piping
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 2001 | 3 | CONCRETE WORKS (STRUCTURAL)
PART CC1
SCHEDULED FORMWORK ITEMS
PSCC1.002 | 3.01 | Smooth
| 3.01.01 | Vertical formwork to
| 3.01.01.01 | Foundations (Floor) | m² | 20
| 3.01.01.02 | Walls | m² | 580
| 3.01.01.03 | Sump | m² | 4
| 3.02.01 | Horizontal formwork to
| 3.02.01.01 | Slabs | m² | 45
PSCC1.005 | 3.02 | Narrow widths (up to 300 mm wide)
| 3.02.01 | Vertical Smooth formwork to
| 3.02.01.01 | Precast slabs | m | 60
PSCC1.006 | 3.03 | Box out holes/form voids
| 3.03.01 | a) Small, circular, of diameter up to 0,35 m
| 3.03.01.01 | 0 m up to and including 0,5 m | No. | 32
| 3.03.02 | d) Large, other than circular, areas over 0.1 m2 up
to 2,0 m2
| 3.03.02.01 | 0 m up to and including 0,5 m | No. | 4
SCHEDULED REINFORCEMENT ITEMS
PSCC1.007 | 3.04 | Steel bars
| 3.04.01 | a) Steel bars irrespective of grade and diameter | t | 24
SCHEDULED CONCRETE ITEMS
PSCC1.011 | 3.05 | Blinding layer in Grade 15 MPa/19 mm concrete
| 3.05.01 | 50 mm thickness | m² | 150
PSCC1.012 | 3.06 | Strength concrete
| 3.06.01 | Class 30 MPa/19 mm concrete in
| 3.06.01.01 | Foundations (Floor) | m3 | 15
| 3.06.01.02 | Walls | m3 | 90
| 3.06.01.03 | Roof slab | m3 | 12
| 3.06.01.04 | Sump | m3 | 2
Carried forward
Part E - Section 1 - Trenchless Piping
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.013 | 3.07 | Unformed surface finishes
| 3.07.01 | a) Steel-floated finish
| 3.07.01.01 | Foundations (Floor) | m² | 40
| 3.07.01.02 | Top of Walls | m² | 15
| 3.07.01.03 | Roof slabs | m² | 45
| 3.07.02 | d) Broomed finish
| 3.07.02.01 | Blinding layer | m² | 150
| 3.07.03 | e) Screed in 3:1 Sand and Cement Mix
| 3.07.03.01 | Chamber floor screed | m³ | 5
PSCC1.015 | 3.08 | Joints
| 3.08.01 | Polysulphide sealant between precast slab | m | 30
PSCC1.019 | 3.09 | HD bolts and miscellaneous metal work
| 3.09.01 | Fabricate and install galvanised mild steel ladders | No. | 4
(5 m long) as per
Drawing: JW14358-16941-T-017-S09-00-TMS
| 3.09.02 | Fabricate and cast in long inlet airvent (5 m long) as per | No. | 4
Drawing: JW14358-16941-T-017-S09-00-TMS
| 3.09.03 | Fabricate and cast in short outlet airvent as per | No. | 4
Drawing: JW14358-16941-T-017-S09-00-TMS
| 3.09.04 | Fabricate and cast in galvanised access manholes as per | No. | 4
Drawing: JW14358-16941-T-017-S09-00-TMS
| 3.09.05 | Fabricate and cast in lifting hooks as per | No. | 32
Drawing: JW14358-16941-T-017-S10-00-TMS
PSCC1.020 | 3.10 | Colour Mitigation to
| 3.10.01 | Exposed Chambers along roadways | m² | 60
MISCELLANEOUS ITEMS
PSCC1.021 | 3.11 | Polythene sheeting under concrete
| 3.11.01 | 250 micron green medium density polyethylene | m² | 150
dampproof sheeting
PSCC1.023 | 3.12 | FRP items
| 3.12.01 | a) FRP Grating
| 3.12.01.01 | 450 mm x 450 mm x 38 mm deep FRP grating | m² | 4
Carried forward
Part E - Section 1 - Trenchless Piping
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.025 | 3.13 | Installation of precast elements
| 3.13.01 | Precast roof slabs | No. | 8
PSCC1.027 | 3.14 | Masonry
| 3.14.01 | 110 mm brick wall | m² | 10
| 3.14.02 | 220 mm brick wall | m² | 20
Carried forward to summary (Part E - Section 1)
Part E - Section 1 - Trenchless Piping
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SUMMARY
SANS 1200 LG |  | PIPE JACKING
SANS 1200 L |  | MEDIUM-PRESSURE PIPELINES
SANS 2001 CC1 |  | CONCRETE WORKS (STRUCTURAL)
Total carried forward to summary

## Concrete Tunnel
Part E - Section 2 - Concrete Pipe Tunnel
Site Clearance
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 C | 1 | SITE CLEARANCE
Refer to Drawing:
JW14358-16941-T-014-S12-00-TMS
PSC 8.2.12 | 1.01 | Removal of man-made surfaces and kerbing
| 1.01.01 | c) Interlocking concrete segmental paving blocks, | m² | 220
Class 2.6/40MPa (all colours)
PSC 8.2.13 | 1.01 | Backfilling and reinstatement of man-made surfaces
re-using removed materials
| 1.01.01 | a) Interlocking concrete segmental paving blocks, | m² | 80
Class 2.6/40MPa (all colours)
PSC 8.2.14 | 1.04 | Take down and re-erect existing fences and
guardrails
| 1.04.01 | a) Guardrails | m | 50
| 1.04.02 | b) Diamond mesh fencing | m | 50
Carried forward to summary (Part E - Section 2)
Part E - Section 2 - Concrete Pipe Tunnel
Earthworks
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 1200 DB | 2 | EARTHWORKS
PSDB 8.3.3 | 2.01 | Restricted excavation
| 2.02.01 | a) Excavate for restricted foundations, footings and
pipe trenches in all materials and use for backfill or
embankment or dispose
| 2.02.01.01 | Concrete Pipe Tunnel | m³ | 270
PSDB 8.3.3 | 2.02.02 | b) Extra over for
| 2.02.02.01 | 1) intermediate excavation | m³ | 30
| 2.02.02.02 | 2) hard rock excavation | m³ | 30
PSDB 8.3.3 | 2.02.02.03 | 3) Hand excavation where ordered by the Project
Manager
| 2.02.02.03.01 | a) Soft material | m³ | 30
| 2.02.02.03.02 | b) Intermediate material | m³ | 30
| 2.02.02.03.03 | c) Hard material | m³ | 30
PSDB 8.3.3 | 2.02.02.04 | 4) Backfill stabilized with 5% cement where directed by | m³ | 60
the Project Manager
PSDB 8.3.3 | 2.02.02.05 | 5) Soilcrete backfill where directed by the Project | m³ | 60
Manager
PSDB 8.3.6 | 2.02 | Finishing
PSDB8.3.6.1 | 2.02.01 | Reinstate road surfaces complete with all courses
| 2.02.01.01 | f) Re-instatement of bricks, concrete pre-cast units and | m² | 80
interlocking concrete segmental paving
Carried forward to summary (Part E - Section 2)
Part E - Section 2 - Concrete Pipe Tunnel
Concrete works (structural)
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SANS 2001 | 5.00 | CONCRETE WORKS (STRUCTURAL)
PART CC1
SCHEDULED FORMWORK ITEMS
PSCC1.002 | 5.01 | Smooth
| 5.01.01 | Vertical formwork to
| 5.01.01.01 | Foundations (Floor) | m² | 150
| 5.01.01.02 | Walls | m² | 700
| 5.01.01.03 | Plinths | m² | 30
| 5.01.02 | Horizontal formwork to:
| 5.01.02.01 | Floors / Roofs | m² | 270
PSCC1.006 | 5.02 | Box out holes/form voids
| 5.02.01 | d) Large, other than circular, areas over 0.1 m2
up to 2,0 m2
| 5.02.01.01 | 0 m up to and including 0,5 m | No. | 3
SCHEDULED REINFORCEMENT ITEMS
PSCC1.007 | 5.03 | Steel bars
| 5.03.01 | a) Steel bars irrespective of grade and diameter | t | 30
PSCC1.008 | 5.04 | High-tensile welded mesh
| 5.04.01 | Mesh Ref 395 | m² | 25
SCHEDULED CONCRETE ITEMS
PSCC1.011 | 5.05 | Blinding layer in Grade 15 MPa/19 mm concrete
| 5.05.01 | 50 mm thickness | m² | 120
PSCC1.012 | 5.06 | Strength concrete
| 5.06.01 | Class 30 MPa/19 mm concrete in:
| 5.06.01.01 | Foundation (Floor) / Roof | m3 | 75
| 5.06.01.02 | Walls | m3 | 60
| 5.06.01.03 | Plinths | m3 | 6
Carried forward
Part E - Section 2 - Concrete Pipe Tunnel
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.013 | 5.07 | Unformed surface finishes
| 5.07.01 | a) Steel-floated finish
| 5.07.01.01 | Floor / Roof | m² | 210
| 5.07.01.02 | Top of Plinths | m² | 20
| 5.07.01.03 | Top of Walls | m² | 70
| 5.07.02 | d) Broomed finish
| 5.07.02.01 | Blinding layer | m² | 120
PSCC1.015 | 5.08 | Joints
| 5.08.01 | 10 mm thick bitumen impregnated fibre board | m² | 25
| 5.08.02 | 10 mm x 10 mm Polyurethane Sealant | m | 110
PSCC1.018 | 5.09 | Grouting
| 5.09.01 | a) Under bases of pipe supports and straps | m³ | 2
| 5.09.02 | c) Pipe box-outs | m³ | 2
PSCC1.019 | 5.10 | HD bolts and miscellaneous metal work
| 5.10.01 | Fabricate and install galvanised mild steelbase plate and | No. | 24
support bracket as per
Drawing: JW14358-16941-T-014-S11-00-TMS
| 5.10.02 | Fabricate and install galvanised mild steel fastening strap, | No. | 24
including bolts as per
Drawing: JW14358-16941-T-014-S11-00-TMS
| 5.10.03 | Fabricate and cast in lifting hooks | No. | 60
PSCC1.020 | 5.11 | Colour Mitigation to
| 5.11.01 | Exposed tunnel sections along roadways | m² | 150
MISCELLANEOUS ITEMS
PSCC1.021 | 5.12 | Polythene sheeting under concrete
| 5.12.01 | 250 micron green medium density polyethylene | m² | 120
dampproof sheeting
PSCC1.024 | 5.13 | Casting pipes and specials in concrete
| 5.13.01 | DN 250 Steel pipe cast into chamber wall | No. | 1
| 5.13.02 | DN 600 Steel pipe cast into chamber wall | No. | 2
| 5.13.03 | Fabricate and cast in lifting hooks | No. | 60
Carried forward
Part E - Section 2 - Concrete Pipe Tunnel
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
Brought forward
PSCC1.025 | 5.14 | Installation of precast elements
| 5.14.01 | Precast tunnel sections as per | No. | 26
Drawing: JW14358-16941-T-014-S11-00-TMS
`
Carried forward to summary (Part E - Section 2)
Part E - Section 2 - Concrete Pipe Tunnel
PAYMENT | ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
REFERS TO | NO
SUMMARY
SANS 1200 C |  | SITE CLEARANCE
SANS 1200 DB |  | EARTHWORKS
SANS 2001 CC1 |  | CONCRETE WORKS (STRUCTURAL)
Total carried forward to summary

## Summary
Johannesburg Water (SOC) Ltd
JW14358 - Construction of Woodmead Inlet Bulk
Summary of Schedule of Quantities
ITEM NO | DESCRIPTION | AMOUNT
SUMMARY
1 | PART A - GENERAL
1.1 | Part A - Section 1: Preliminary and general | R
2 | PART B - PIPELINES
2.1 | Part B - Section 1: DN 600 Steel Main Pipeline | R
2.2 | Part B - Section 2: DN 600 Steel Bypass Pipeline | R
2.3 | Part B - Section 3: DN 800 Steel Pipeline | R
2.4 | Part B - Section 4: DN 200 High Impact mPVC Pipeline | R
3 | PART C - CHAMBERS
3.1 | Part C - Section 1 - Scour Valve Chamber 1 and 2: NA13, NA23, NA41, NA64, NA81, NA95, NB10 | R
3.2 | Part C - Section 2 - Air Valve Chambers: Nodes NA15,21,39,45,57,69,85,94,97, NC11 | R
3.3 | Part C - Section 3 - DN 200 Flow Meter and scour Valve Chamber: Node NC3 | R
3.4 | Part C - Section 4 - DN 800 isolation, scour and future tie-in chamber: Node ND2 | R
3.5 | Part C - Section 5 - Hot-Tapping chambers: Node NA1, ND1, ND5 | R
3.6 | Part C - Section 6 - Upgrades to Existing Butterfly Valve Chambers | R
3.7 | Part C - Section 7 - PRV, NRV and FM chamber: Node NA4, NB11, NC26, NC25 | R
3.8 | Part C - Section 8 - Tie-in chambers: Node NA103, NB12 | R
4 | PART D - CATHODIC PROTECTION AND AC MITIGATION
4.1 | Part D - Portion 1 - Cathodic Protection | R
5 | PART E - TRENCHLESS PIPING
5.1 | Part E - Section 1 - Trenchless Piping | R
5.2 | Part E - Section 2 - Concrete Pipe Tunnel | R
| Sub-Total 1 TOTAL FOR SCHEDULE OF QUANTITIES | R
PSA 8.9 | The above prices are Not Firm. In respect of the total value of work done by approved SMME’s at 30% of Sub Total 1 (This total shall include all amounts payable to SMME’s, including P&G’s) = R………………………………………………………………......................…… (A) Allowance as a percentage (maximum 15%) for appointing and handling work done by approved SMME’s …………………………………………………….......................………………% (B)
| Sub-Total 2 [ Handling fees for subcontracting = (A) x (B) ] | R
| Sub-Total 3 = Sub Total 1 + Sub Total 2 | R
ADD | Escalation @ 10% | R
| Sub-Total 4 = (Sub 3 + Escalation @ 10%) | R
ADD | Contingencies @ 10% | R
| Sub-Total 5 = (Sub 4 + Contingencies @ 10%) | R
ADD | 15% VAT | R
| TOTAL | R
`